## HR Evaluation Factor
OIL INDIA LIMITED
3X10 MW POWER PLANT EXTENSION AT DULIAJAN
HEAT RATE ADJUSTMENT CALCULATION DUE TO INCREASE IN NET HEAT RATE BY 1 KCAL/KWH
| INCREASE IN HEAT RATE NET |  |  | 1 | KCAL/KWH
| AUXILIARY POWER CONSUMPTION |  |  | 2 | %
| INCREASE IN HEAT RATE GROSS |  |  | 1.0204 | KCAL/KWH
ANNUAL OPERATING HOURS FACTOR |  | 0.8
POWER STATION SIZE-NET |  | 24.4 | MW | 170.9952 | MU/YEAR
FUEL GAS CALORIFIC VALUE |  | 8700 | KCAL/SCUM
FUEL COST INCREASE PER YEAR % |  |  | 6
YR | FUEL COST | FUEL COST | ENERGY | TOTAL CST
| RS/SCM | RS | MU | MRS
1 | 6.5 | 0.00076237 | 170.9952 | 0.13036
2 | 6.89 | 0.00080812 | 170.9952 | 0.13818
3 | 7.3034 | 0.0008566 | 170.9952 | 0.14648
4 | 7.7416 | 0.000908 | 170.9952 | 0.15526
5 | 8.2061 | 0.00096248 | 170.9952 | 0.16458
6 | 8.6985 | 0.0010202 | 170.9952 | 0.17445
7 | 9.2204 | 0.0010814 | 170.9952 | 0.18492
8 | 9.7736 | 0.0011463 | 170.9952 | 0.19602
9 | 10.36 | 0.0012151 | 170.9952 | 0.20778
10 | 10.9816 | 0.001288 | 170.9952 | 0.22024
11 | 11.6405 | 0.0013653 | 170.9952 | 0.23346
12 | 12.3389 | 0.0014472 | 170.9952 | 0.24747
13 | 13.0793 | 0.001534 | 170.9952 | 0.26231
14 | 13.864 | 0.0016261 | 170.9952 | 0.27805
15 | 14.6959 | 0.0017237 | 170.9952 | 0.29474
16 | 15.5776 | 0.0018271 | 170.9952 | 0.31242
17 | 16.5123 | 0.0019367 | 170.9952 | 0.33117
18 | 17.503 | 0.0020529 | 170.9952 | 0.35104
19 | 18.5532 | 0.0021761 | 170.9952 | 0.3721
20 | 19.6664 | 0.0023066 | 170.9952 | 0.39442
21 | 20.8464 | 0.002445 | 170.9952 | 0.41809
22 | 22.0972 | 0.0025917 | 170.9952 | 0.44317
23 | 23.423 | 0.0027472 | 170.9952 | 0.46977
24 | 24.8284 | 0.0029121 | 170.9952 | 0.49795
25 | 26.3181 | 0.0030868 | 170.9952 | 0.52783
DISCOUNT RATE |  | 10 | %
NPV |  | 2.1649 | MRS/KCAL/KWH
|  | 88.7245 | RS/KCAL/KWH/KW
HEAT RATE EVALUATION FACT |  | 88.7245 | RS/KCAL/KWH/KW
HEAT RATE PENALTY @120% OF NPV |  | 106.4694 | RS/KCAL/KWH/kW

## Lube Oil Evaluation Factor
OIL INDIA LIMITED
3X10 MW POWER PLANT EXTENSION AT DULIAJAN
LUBE OIL ADJUSTMENT CALCULATION DUE TO INCREASE IN 1 MG/KWH
| INCREASE IN LUBE OIL |  |  | 1
| COST OF LUBE OIL |  |  | 114
0.000114
ANNAUAL OPERAING HOURS FACTOR |  | 0.8
POWER STATION SIZE-NET |  | 24.4 | MW | 170.9952
LUBE OIL COST INCREASE PER YEAR % |  |  | 6
YR | LO COST | LO COST | ENERGY | TOTAL CST
| RS/KG | RS/KWH | MU | MRS
1 | 114 | 0.000114 | 170.9952 | 0.019493
2 | 120.84 | 0.00012084 | 170.9952 | 0.020663
3 | 128.0904 | 0.00012809 | 170.9952 | 0.021903
4 | 135.7758 | 0.00013578 | 170.9952 | 0.023217
5 | 143.9224 | 0.00014392 | 170.9952 | 0.02461
6 | 152.5577 | 0.00015256 | 170.9952 | 0.026087
7 | 161.7112 | 0.00016171 | 170.9952 | 0.027652
8 | 171.4138 | 0.00017141 | 170.9952 | 0.029311
9 | 181.6987 | 0.0001817 | 170.9952 | 0.03107
10 | 192.6006 | 0.0001926 | 170.9952 | 0.032934
11 | 204.1566 | 0.00020416 | 170.9952 | 0.03491
12 | 216.406 | 0.00021641 | 170.9952 | 0.037004
13 | 229.3904 | 0.00022939 | 170.9952 | 0.039225
14 | 243.1538 | 0.00024315 | 170.9952 | 0.041578
15 | 257.7431 | 0.00025774 | 170.9952 | 0.044073
16 | 273.2076 | 0.00027321 | 170.9952 | 0.046717
17 | 289.6001 | 0.0002896 | 170.9952 | 0.04952
18 | 306.9761 | 0.00030698 | 170.9952 | 0.052491
19 | 325.3947 | 0.00032539 | 170.9952 | 0.055641
20 | 344.9183 | 0.00034492 | 170.9952 | 0.058979
21 | 365.6134 | 0.00036561 | 170.9952 | 0.062518
22 | 387.5503 | 0.00038755 | 170.9952 | 0.066269
23 | 410.8033 | 0.0004108 | 170.9952 | 0.070245
24 | 435.4515 | 0.00043545 | 170.9952 | 0.07446
25 | 461.5785 | 0.00046158 | 170.9952 | 0.078928
DISCOUNT RATE |  | 10 | %
NPV |  | 0.32372 | MRS/MG/KWH
|  | 13.2672 | RS/MG/KWH/KW
LUBE OIL EVALUATION FACT |  | 13.2672 | RS/MG/KWH/KW
LUBE OIL PENALTY @120% OF NPV |  | 15.9207 | RS/MG/KWH/kW