| ELECTRICAL |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| 1 | 1190 -E-DB-0900 | ELECTRICAL DESIGN PHILOSOPHY | All the areas within the battery limits shall be classified for the degree and the extent of hazard from flammable materials | Please note that as a standard practice, all the reputed suppliers provide for adequate ventilation system in the plant room / enclosure where the gas gensets are placed to disperse accumulation of any flamable gas and to make the gas genset plant room / enclosure a non hazourdous zone. Please note that for all the gas genset manufacturer / suppliers, this is non standard. The electrical equipments shall be selected suitably as per non hazourdous classification. | Gas Engine Genset may fall under hazardous area. Hazardous area classification area will be provided as an addendum to the Tender. |
| 2 | 1190 -E-DB-0900 | ELECTRICAL DESIGN PHILOSOPHY | Electrical equipment for hazardous areas shall be certified by CIMFR/ CPRI/ ERTL or equivalent recognized independent test house such as BASEEFA/ LCIE/ LCIE/ PTB/ UL/ FM. | Electrical equipment shall be selected for non hazardous area, therefore the given certification for each equipments are not applicable | Please follow Tender Document. |
| 3 | 1190 -E-DB-0900 | ELECTRICAL DESIGN PHILOSOPHY | EMERGENCY POWER SUPPLY : Emergency power supply could be from a different power source or Emergency generator. Where emergency generator is envisaged, emergency power supply shall be made available within a time period of 30 seconds from the instant of failure of normal supply. | OIL to clarify whether emergency power shall be provided by them ot it is in the bidder's scope. | UPS backup is required for critical emergency instrumentations. Emergency Power shall be provided through Diesel Engine Generator, which is in the scope of EPC. Refer electrical SLD |