| GENERAL |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| 1 | GAS ENGINE GENERATOR |  |  | Site altitude mentioned is 1000 metersà please cross check and re-confirm | Finished Grade level for proposed site is 118.4m from MSL |
| 2 | GAS ENGINE GENERATOR |  |  | Operation philosophy: The proposed gas genset is to run only in Island mode and running in synchronization with Grid Power not envisaged. Please confirm. | There is no Grid power available for the Plant. Power from Gas Generator fullfill the requirement of the Plant. |
| 3 | GAS ENGINE GENERATOR |  |  | Please confirm that water is available on continuous basis required for the engine cooling and inlet air cooling. So that wet type ventilation system shall be proposed for engine room cooling. | Sufficient quantity of Utility water is available at Site. |
| 4 | GAS ENGINE GENERATOR |  |  | Installation of gas genset is in civil constructed room/power plant à please confirm | Structural steel sheds with RCC foundation. |
| 5 | GAS ENGINE GENERATOR |  |  | 2000 kWe output of the gas genset is net output after deduction gas genset auxiliary power consumption and is at 11 kV, 0.8 power factor and at site condition à Please confirm. | Generator shall be at 415V,3PH,50Hz. No other requirements is accepted. |
| 6 | GAS ENGINE GENERATOR |  |  | Generation voltage: As per the enquiry document, generation voltage is 415 V, considering total power generation of 4 MW (2 Nos. x 2 MW) we propose generation at either 6600 V or 11000 V. Please confirm. | Generator shall be at 415V,3PH,50Hz. There are no requirment for 6000V/11000V. |
| 7 | GAS ENGINE GENERATOR |  |  | Doc 1190 – M-TS -0512 – 01 Requisition for quotation for Gas Engine Generator: Page no. 10 , 11 of 31, clause 3.3 Equipment Qualification Criteria: The clause describes qualification requirement of compressor. Please provide qualification requirement of gas genset. | Noted. Revised document will be provided. |
| 8 | GAS ENGINE GENERATOR |  |  | Doc 1190 – M-TS -0512 – 01 Requisition for quotation for Gas Engine Generator: Page 15 of 31, clause 3.8.6: Area classification – Zone 1, Apparatus IIA & IIB, Temperature class T3 à As per manufacturer’s standard design gas gensets are suitable to install in SAFE AREA including all electrical items of Balance of Plant Equipment. Please confirm your acceptance. | Not accepted. Generator shall be suitable for hazardous area location. |
| 9 | GAS ENGINE GENERATOR |  |  | It is observed that in the enquiry few requirements/specifications are mentioned with reference to turbine driven generator / Diesel generator etc. à Trust the same are not applicable for gas genset. Please confirm | Noted. Revised document will be provided. |