| MECHANICAL |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| 1 | Part 3 - Section II of ITB | 91 | Line Schedule | Please furnish the Line Schedule indicating line Pressure, Temperature, Fluid density, etc. which may be available as FEED document. | It is part of EPC’s scope |
| 2 | Part 3 - Section II of ITB | 103 | Mandatory / Recommended Spares | Please furnish the list of Mandatory Spares Equipment / Package wise if Client do have, otherwise that will be as per Equipment / Package Vendors' list. | It is part of EPC’s scope Refer clause 35.0 of ITB, |
| 3 | Vent and Drain philosophy Doc. 1190-P-GD-0100-05 Rev.C | 12 | Hydrotesting Vent and Drain | It's mentioned that Vent required only for hydrotesting may be plugged without valve. Please confirm that drain required only for hydrotesting may also be plugged without valve. | It is confirmed that drain required only for hydrotesting shall be plugged without valve. |
| 4 | Process Design Basis doc 1190-P-DB-0100 Rev.C | 56 | Rain fall data | No data regarding rain fall is found in the document. Please furnish. | Refer Assam Geographical data from government website. |
| 5 |  |  | Sleeper Height | Please advise the minimum height of sleeper from FGL | Minimum 500 mm shall be considered above FGL |
| 6 | Mechanical Design Philosophy doc 1190-M-DB-0500 Rev.C | 20 & 26 | Manhole | In clause 13.1.1.9 for Unfired Pressure Vessel, it's mentioned of atleast DN600 of Manhole size, but In clause 13.1.4 of Tank, it's mentioned of min. DN500 of Manhole size. But we will follow ASME Section VIII code requirement for finalising Manhole size for Pressure Vessels. OIL to advise. | Follow as per respective Equipment data sheet. |
| 7 | Mechanical Design Philosophy doc 1190-M-DB-0500 Rev.C | 15 & 21 | Requrement of Davit and Hinge for Manhole and Inspection Opening | In page no. 15, limit is mentioned as 25 Kg , in page 21, that's as 30 Kg. Please confirm which limit would be considered. | Consider limit is 25kg |
| 8 | DATASHEET – CRUDE STORAGE TANKS (BBJ-1060 C)1190-M-DS-0501-16 | 4 of 06 | CONICAL FLOATING ROOF TANK | Please confirm whether tank is external floaitng roof tank or cone roof with internal floating roof or cone roof tank | external floating roof |
| 9 | DATASHEET – CRUDE STORAGE TANKS (BBJ-1060 C)1190-M-DS-0501-16 | 4 of 06 | 1000 KL | Please confirm whether this volume is stored liquid volume or pumpable volume. | It is storage volume of tank |
| 10 | DATASHEET – CRUDE STORAGE TANKS (BBJ-1060 C)1190-M-DS-0501-16 | 4 of 06 | Anode | We understood that sacrificial anode type CP shall be provided on the soil side of the bottom plate and tank inside also. Please confirm. Please clarify the purpose of the nozzle for sacrificial anode as the anode generally welded with the tank plate itself. Please elaborate. | Sacrificial anode type CP shall be provided on the soil side of the bottom plate and tank inside. The nozzle requirement shall be freezed during detail engineering based on the selection of anode type. |
| 11 | DATASHEET – FOAM CONCENTRATE STORAGE TANK1190-M-DS-0504-04 |  | SA 516 Gr 70N | As the foam is very corrosive in nature, hence the MOC of Foam Tank is generally SS. Hence Please confirm the MOC of the Foam Bladder tank. If it is SS then whether corrosion allowance need to be considered or not. | It shall be SA 516 Gr 70N only |
| 12 | DATASHEET – CRUDE STORAGE TANKS (BBJ-1060 A/B)190-M-DS-0501-11 | 4 of 06 | CONICAL FLOATING ROOF TANK | Please confirm whether tank is external floaitng roof tank or cone roof with internal floating roof or cone roof tank | external floating roof |
| 13 | DATASHEET – CRUDE STORAGE TANKS (BBJ-1060 A/B)190-M-DS-0501-11 | 4 of 06 | 2000 KL | Please confirm whether this volume is stored liquid volume or pumpable liquid volume. | Refer sl no 9 above. |
| 14 | DATASHEET – CRUDE STORAGE TANKS (BBJ-1060 A/B)190-M-DS-0501-11 | 4 of 06 | Anode | We understood that sacrificial anode typre CP shall be provided on the soil side of the bottom plate and tank inside also. Please confirm. Please clarify the purpose of the nozzle for sacrificial anode as the anode generally welded with the tank plate itself. Please elaborate. | Refer sl no 10 above. |
| 15 | DATA SHEET –TREATED WATER STORAGE TANK (ABJ-1150A/B/C) 1190-M-DS-0502-03 | 4 of 5 | 2000 KL | Please confirm whether this volume is stored liquide volume or pumpable volume. | Refer sl no 9 above. |
| 16 | Genral |  | CrudeTanks | Please confirm design specific gravity of the all crude tanks. Whether it will 1 or SP. Gr. of the curde. | Since the design pressure of storage tank is FOW, the design Sp. Gravity shall be 1. |
| 17 | Fire Protection |  | Design Basis | Please provide the fire protection design basis of the project. Though Water & Foam based fire protection P &Ds is available. But Specification or Design Basis is available for Protable Fire Protection System & control room, substance, building fire protection details. | Details will be provided. |
| 18 | 1190-L-DW-0400 - EQUIPMENT LAYOUT - OVERALL PLOT PLAN |  | B/L Co ordinate | Please provide battery limit of co-ordinate for piping scope. | Question not clear. However, Battery Limit for piping starts from Inlet manifold. |
| 19 | 1190-L-DW-0400-03 - EQUIPMENT LAYOUT - AREA LAYOUT |  | Ground Flare Tip, Associated Pipe sleeper and boundary layout | This area layout is different from Overall Plot Plan. We understand that Overall Plot Plan would be followed. Please confirm. | It is the enlargement of the same area. No difference between the two. |
| 20 |  |  | Painting and Color coding Specification | Please provide OIL standard Painting and Color coding Specification | Will be provided in the painting specification as addendum to tender. |
| 21 | Mechanical section of Tender docs/ Bid docs |  | Data sheet for Pumps | Data sheets of pumps with Tag nos. PBA-1220 A/B, PBA-1400 A/B , PBA-1553 A/B & PBA-2157 A/B are not covered under Tender documents. Please provide the same. | Will be issued as addendum |
| 22 | Mechanical section of Tender docs/ Bid docs |  | Data sheet/ specifications for Crane /Hoist | Data sheets for Crane /Hoist are not covered under Tender documents. Please provide the same. | DS for EOT crane will be provided |
| 23 | Mechanical Design Philosophy doc 1190-M-DB-0500 Rev.C | 30 | Type of Hoist | It's mentioned that for equipment / parts heavier than 500 Kg shall be handled by permanent provision of lifting lugs, trolley, and hoist e.t.c. Client to confirm. We understand that Manual (Not Electrical) Hoist would be provided. | It shall be studied by EPC during Detail engineering. |
|  | Mechanical section of Tender docs/ Bid docs |  | HVAC | Requirement HVAC system is not covered under Tender documents . Please arrange to provide necessary specifications/ data sheets alongwith the locations for the same. | Split A/c is considered. |
| 24 | Mechanical section of Tender docs/ Bid docs |  | Ground flare | Data sheet/ specification is not covered under Tender documents .Please arrange to provide necessary specifications/ data sheets for the same. Can we provide as per decription & information avilable under equipment list, mechanical design philosophy & process design philosophy etc.? | Data sheets will be provided. |
| 25 | Mechanical section of Tender docs/ Bid docs |  | Hot Oil Heater (TAG No. MBK-2070) for Hot Oil Package | Data sheet/ specification is not covered under Tender documents .Please arrange to provide necessary specifications/ data sheets for the same.Can we provide as per decription & information avilable under equipment list, mechanical design philosophy & process design philosophy etc.? | It is Gas fired Hot oil heater. Revised data sheet will be issued. |
|  | Mechanical section of Tender docs/ Bid docs |  | Blower ( TAG No. B-2080 A/B) | Data sheet/ specification is not covered under Tender documents .Please arrange to provide necessary specifications/ data sheets for the same.Can we provide as per decription & information avilable under equipment list, mechanical design philosophy & process design philosophy etc.? Also furnish tenative capacity & pressure of Blower for civil & structural estimation purpose. | Will be provided as addendum |
| 26 | Mechanical section of Tender docs/ Bid docs |  | Blower ( TAG No. B-A-1460 A/B,B-B-1460 A/B,B-A-1490-A/B & B-B-1490-A/B) | Data sheet/ specification is not covered under Tender documents .Please arrange to provide necessary specifications/ data sheets for the same.Can we provide as per decription & information avilable under equipment list, mechanical design philosophy & process design philosophy etc.? Also furnish tenative capacity & pressure of Blower for civil & structural estimation purpose. | Will be provided as addendum |
| 27 | Mechanical section of Tender docs/ Bid docs |  | RO WATER MAKER ( ZZZ-1380 A/B) | Data sheet/ specification is not covered under Tender documents .Please arrange to provide necessary specifications/ data sheets for the same.Can we provide as per decription & information avilable under equipment list, mechanical design philosophy & process design philosophy & industry std. etc.? | Will be provided as addendum |
| 28 | Mechanical section of Tender docs/ Bid docs |  | UV STERILIZER UNIT(ZZZ-1420) | Data sheet/ specification is not covered under Tender documents .Please arrange to provide necessary specifications/ data sheets for the same.Can we provide as per decription & information avilable under equipment list, mechanical design philosophy & process design philosophy & industry std. etc.? | Will be provided as addendum |
| 29 | 1190-M-DS-0502-06 ,1190-M-DS-0502-10,1190-M-DS-0501-14,1190-M-LL-0500 |  | TREATED WATER DISPOSAL PUMPS(PBA-1160 A/B),POTABLE WATER PUMPS(PBA-1400 A/B),TEST TANK TRANSFER PUMP(PBA-1553 A/B),CLOSED DRAIN KOD TRANSFER PUMPS(PBA-2157 A/B) | We understand that for water applications API Pumps are not required. Any Non API Pump can serve the purpose satisfactorily. Therefore please clarify whether we can go for Non API Pumps for Water applications or not. Also note that for Water pump generally gland packing with stuffing box is used for shaft sealing purpose. Mechanical seal is not necessary. OIL /EPMC to review and confirm / clarify. | Please follow the respective data sheet. |
| 30 | 1190-M-DS-0504-03,1190-M-DS-0504-02,1190-M-LL-0500 |  | Diesel Engine Driven Main Fire Water Pumps (PAB-1620 A/B),Motor Driven Jockey Pump (PBA-1630 A/B ) | Differential pressure of both pumps as 8 kg/cm2 mentioned in Equipment List, seems to be insufficient. Therefore requesting Client to recheck & reconfirm the same. Also Client to check & confirm the data given in Jockey Pump data sheet. | Differential pressure of both pumps FW Pump and Jockey Pump) shall be 9 kg/cm2. Revised data sheets will be issued as addendum. |
| 31 | 1190-M-LL-0500 & ITB (Cost sheet item no. A.3.6) |  | Main fire water pump quantity | In the Cost sheet item no. A.3.6, the quantities mentioned is 3 no.s, whereas in the equipment list the description & the quantity is 2 no.s. Request you to kindly clarify the quantity. | Confirmed . Qty is 2 No’s |
| 32 | Part 3 - Section II of ITB | 83 | Tank Materials | It's stated that "Grade 316 L SS shall be used for water storage tanks and lubrication oil tanks" But as per Water Tank Data sheets, CS ( A 283 Gr.C) is mentioned. We are going ahead with materials as per Data Sheets for Water and other Tanks. Client to confirm | CS for Ind. Water tank and SS 316L for Potable water tank shall be considered |
| 33 | Mechanical Design Philosophy doc 1190-M-DB-0500 Rev.C | 18 | Wind and Seismic data | We are not considering ASCE-07 for wind load & Seismic Load. We are following IS 875 (Part -3) for Wind & IS 1893 for Seismic. Please advise. | IS 875 (Part -3) for Wind & IS 1893 for Seismic shall be followed. |
| 34 | 1190-P-DW-1101 Rev.D | 1 of 1 | IA/UA Compressor | i) As per Utility consumption schedule (1190-P-SH-0100 Rev.C, Cl. no. 2.1 & 2.2) Design Temperature for Utility Air & Instrument Air is 80 deg C. But the Design Temperature considered for Compressor is 150 deg C. The basis for selecting such high Design Temperature may please be provided. ii) Compressor Power given in P&ID is not matching with the Compressor Package DS(1190-M-TS-0505-01 Rev.A) and Equipment List(1190-M-LL-0500 Rev.D). We consider Equipment List/Datasheet value is updated. Please confirm. | IA Comp. package shall be designed for 150 deg C upto its battery limit. Receiver/ dryer package shall be designed for 80 deg. C Rev-D P & I Ds shall be followed |
| 35 | 1190-M-DS-0505-01 Rev.A | 4,6 of 7 | Utility Air Receiver | i) Diameter & T/T length in Datasheet is 2286 mm & 10500 mm respectively. But in P&ID(1190-P-DW-1102 Rev.D) & Equipment List(1190-M-LL-0500 Rev.D) Diameter is 2600 mm & T/T length is 7800 mm. Please confirm which document is to take as updated. ii) We consider Utility Air receiver Capacity 600 Nm3/hr, though it is given as 600 m3/hr in datasheet. Please confirm. | Rev-D P & I Ds shall be followed. |
| 36 | 1190-M-DS-0505-02 Rev.A | 4,6 of 7 | Instrument Air Receiver | i) Diameter & T/T length in Datasheet is 2184 mm & 8600 mm respectively. But in P&ID(1190-P-DW-1102 Rev.D) & Equipment List(1190-M-LL-0500 Rev.D) Diameter is 2400 mm & T/T length is 6900 mm. Please confirm which document is to take as updated | Rev-D P & I Ds shall be followed |
| 37 | 1190-P-DW-1001, Rev D |  | Fire water Storage Tank | We have considered storage tank in two equal interconnected compartments as per OISD 189 & one level transmitter in storage tank. Pls confirm. | The Fire Water storage tank shall be single compartment only. |
| 38 | 1190-M-DS-0504-03 | 4,5 of 9 | Fire water pumps | Please clarify basis of material selection & basis of area classification of Fire water pumps. | As per P&ID |
| 39 | 1190-M-DS-0504-02 | 4,5 of 9 | Fire water Jockey pumps | Please clarify basis of material selection & basis of area classification of Fire water Jockey pumps. | As per P&ID |
| 40 | 1190-M-DS-0504-02 | 4 of 9 | Motor KW | As per pump datasheet hydraulic power is 15.5 Kw. But motor Kw (Nameplate power) is 750 Kw. The basis of selection of such high motor kw may please be provided. | Typo error. Vendor to confirm the size. |
| 41 | 1190-M-DS-0509-02 | 7 of 7 | Nozzle schedule of Hot oil filter (MAJ-2050) | K1 nozzle as mentioned in the P&ID (1190-P-DW-0701 Rev D) to be added in the nozzle schedule . | Revised DS will be issued as an addendum. |
| 42 | 1190-M-DS-0509-01 | 7 of 7 | Nozzle schedule of Hot oil expansion vessel (MBD-2040) | N9 nozzle for utility connection as mentioned in the P&ID (1190-P-DW-0701 Rev D) to be added in the nozzle schedule . | Revised DS will be issued as an addendum. |
|  | 1190-M-DS-0509-04 | 7 of 7 | Nozzle schedule of Hot oil drain tank (MBD-2040) | 2" N3 nozzle as mentioned for hot oil vapour to MBD 3207B is a repeatation and not found in P&ID (1190-P-DW-0703 Rev D). Please confirm. | Revised DS will be issued as an addendum. |
| 43 | 1190-M-DS-0509-04 |  | Design pressure of Hot oil system. | Design pressure of hot oil system is considered as 12.5 kg/cm2g.Please confirm. | 12.5 kg/cm2g is correct. Follow as per latest P&ID. |
| 44 | 1190-P-DW-1009 |  | PMS & MOC of ABJ-2130 | Please ensure that ABJ-2130 & all foam lines are CS material. | As per Rev-D P&ID it is CS. |
| 45 |  |  | Process pumps & Gas compressor | We have considered all process pumps & gas compressor as air cooled. Please confirm. | It shall be vendor specific. |
| 46 | 1190-P-DW-1004-1008 |  | Flowmeters in FW lines | Please clarify the provision of flowmeters in distribution line of FW system. | Follow P & I D |
| 47 | 1190-P-DW-1004-1008 |  | MOC of FW distribution lines after XV | We have considered AG70 instead of AC01 piping spec after XV. Please confirm. | AG70 shall be allowed for entire FW distribution lines. |
| 48 | 1190-P-DW-0104 Rev.D | 1 of 1 | Effluent Water System Pump Note in PFD | Note-3 given for Motor Duty of Pump PBA-1220A/B is not found in the PFD sheet. | Motor duty shall be confirmed by vendor based on given absorbed power during detail engineering . |
|  | 1190-P-DW-0903 Rev.D | 1 of 1 | Effluent Water System Pump | i) Pump PBA-1220A/B datasheet not found. Ii) Please clarify the basis for selecting API 610 Code for Effluent Water Pump | Pump PBA-1220A/B datasheet will be provided. The eff. Water will have traces of oil. |
| 49 | 1190-P-DW-0901 Rev.D | 1 of 1 | Effluent Water System Flow Control | i) As per Process description (1190 -P-GD-0100-01 Rev.C, Page 38, Cl. no. 6.0) Effluent "pump starts to run when the pit effluent water level is high". But in Effluent Water System P&ID no instrument is provided to maintain this phylosophy. Please clarify. ii) Please clarify the basis for selecting API 650 Code for Effluent Water Collection Pit | Revised P & I D will be issued to include the level instrument. The tank is RCC only( wrongly mentioned as API 650) |
| 50 | 1190-P-DW-0401 Rev.D | 1 of 1 | Hydrocyclone Sizing Capacity | As per Note 13 in P&ID the Design Flowrate for Hydrocyclone Sizing will be sum of Inlet Flowrate + PW Circulation Pump Capacity + Effluent Water Transfer Pump Capacity i.e (1386+312+180) KLPD = 1878 KLPD. But as per datasheet (1190-M-DS-0502-01 Rev.A) it is 1752 KLPD. Please confirm. | Revised data sheet will be issued to match the P & I D capacity |
| 51 | 1190-M-DS-0502-03 Rev.A | 4 of 5 | Treated Water Storage Tank Outlet Nozzle | Treated Water Outlet nozzle(N2) size is 4'', as per datasheet & P&ID for tank ABJ-1150A(1190-P-DW-0404 Rev.D). But for tank ABJ-1150B(1190-P-DW-0405 Rev.D) & ABJ-1150C(1190-P-DW-0406 Rev.D) N2 is 6''. Please confirm the size of outlet nozzle N2. | N2 size shall be 6” for all tanks. |
| 52 | 1190-M-DS-0502-07 Rev.A | 5 of 9 | Treated Water Disposal Pump Inlet/Outlet Nozzle Connection Rating | Nozzle Rating for Inlet / Outlet connection is given 300#. But the Pump discharge pressure is 12kg/cm2g. The basis for this Rating may please be provided. | API pump rating shall be minimum 300# |
| 53 | 1190-P-DW-0407 Rev.D | 1 of 1 | Pipe Material Spec. | Line spec downstream to Pump PBA-1160A/B is AC01 (Line sequential no. 4357 & 4356). But the Pump discharge pressure is 30kg/cm2g. As per PMS these line spec will be BC01. Please confirm. | Follow BC01 |
| 54 | 1190-P-DW-0218 Rev.D | 1 of 1 | Crude Oil Test Tank Inlet Nozzle Rating | Incoming liquid line(4''-PL-13-0791-BC01) is 300#. We consider Inlet Nozzle N1 as 300#. Hence, no spec break is required. Please confirm. | Tank material spec. is AC01 and piping line material is BC01. Hence spec. break given is correct. |
|  | 1190-P-DW-0219 Rev.D | 1 of 1 | Pipe Material Spec. | Line spec downstream to Pump PBA-1553A/B is AC01 (Line sequential no. 1381 & 1384). But the Pump discharge pressure is 20kg/cm2g. Hence as per PMS we consider the downstream line spec as BC01. Please confirm. | Follow BC01 |
| 55 | 1190-P-DW-0304 Rev.D | 1 of 1 | Inlet Separator-B inlet nozzle spec break | Spec break on line 10''-PL-20-0104-BC01-HC is not required as Inlet nozzle N1 of Inlet Separator-B is 300# as per Datasheet - 1190-M-DS-0501-02 Rev.A. | Up to separator inlet nozzle N1, the material spec. shall be BC01. |
| 56 | 1190-M-LL-0500 Rev.D | 9 of 9 | Datasheet not found | i) ZZZ-1190 - Multiphase Flowmeter DS not found. ii) PBA-1553A/B - Test Tank Transfer Pump DS not found. May please be provided. | Data sheet will be provided. |
| 57 | 1190-M-LL-0500 Rev.D | 8 of 9 | Datasheet not found | i) PBA-1400A/B - Potable Water Pumps DS not found. Ii) PBA-2157 A/B - Closed drain KOD Transfer pump DS not found. | Data sheet will be provided. |
| 58 | 1190-M-TS-0505-02 Rev.A | 15 of 23 | Hazardous Area Clasification for IA Dryer | Zone-2 is given as hazardous area classification in Instrumentation & Controls section. But as per Site Conditions & available utilities (Doc. no. 1190-P-GD-0100-04, Rev.C) Area Classification is Zone 1 for Utilities. Please confirm. | Area Classification is Zone 2 for Utilities. Confirmed. |
| 59 | 1190-P-DW-0602/0604/0605/0608/0609, Rev D |  | PMS-FS70 selection | Please clarify the basis of selecting PMS-FS70 in pipelines below or equal to 30 Kg/cm2g of design pressure. | All the tubing material is considered as FS70. Bidder to follow the same. |
| 60 | 1190-M-LL-0500 Rev.D |  | Chemical injection pump datasheets. | Mismatches are found for differential pressure in Chemical injection pump datasheets & Equipment list. Please confirm. | Data sheet will be revised as per latest P&ID rev.D |