| INSTRUMENTATION |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| 1 | Design Basis - Instrumentation & Control (1190-DB-0801) | 7 of 21 | SIL classification of Interlock and Shut-down system | It is indicated that SIL classification required . Please elaborate, what is intended. Whether SIL 3 PLC is sufficient or all the field devices, i.e. Transmitters / switches in the ESD are also to be SIL certified? | ESD shall be SIL 3 certified PLC . In addition, SIL study to be assesed. All field devices in the ESD shall be SIL certified |
| 2 | Design Basis - Instrumentation & Control (1190-DB-0801) | 7 of 21 | Interaction with Offshore wells & Remote monitoring from Offshore Control Room | Please elaborate on interface with Offshore wells, we understand that it is onshore wells. However, for interface with OCS barekuri DCS, what shall be the modality and licensing of communication ? | Bidder understanding is correct. No offshore well interface. Interface with OCS Barekuri DCS shall be wireless Radio communication |
| 3 | Design Basis - Instrumentation & Control (1190-DB-0801) | 7 of 21 | ESD facilities from Offshore Control Room | Please elaborate “ESD facilities from Offshore Control Room”. | No Offshore Control Room ESD interface. |
| 4 | Design Basis - Instrumentation & Control (1190-DB-0801) | 8 of 21 | Local Panel Requirement | Please reconfirm that Local panel Shall be flameproof , not purged. | Confirmed |
| 5 | Design Basis - Instrumentation & Control (1190-DB-0801) | 9 of 21 | Logic implementation for package Units through | Please confirm whther PLC is envisaged for diff. packages (e.g. Gas Compressor, Instrument Air/Utility Air etc.) | Confirmed. Bidder shall refer to clause 2.0 Package Unit Philosophy Page 8 of 21 of Instrumentation Design Basis |
| 6 | Design Basis - Instrumentation & Control (1190-DB-0801) | 10 of 21 | Number of Operator Consoles for OCS Control Room | It is indicated that 3 Consoles , each with 3 screens , please reconfirm that our scope will be 9 LCD screens, out of which 3 Consoles will be there | Confirmed |
| 7 | Design Basis - Instrumentation & Control (1190-DB-0801) | 11 of 21 | Giant Screen | a) What size is required? b) Where will it be mounted? c) Is it pertaining to CCTV system for Flare monitoring or to be integrated to DCS for key parameters? Please elaborate. | Giant screen size shall be minimum 56”. Same shall be finalized during detail engineering stage. Giant screen pertaining to CCTV and DCS. |
| 8 | Design Basis - Instrumentation & Control (1190-DB-0801) | 11 of 21 | Foreign Device Interface with DCS | As per this clause their shall be a separate alarm management system which shall be interfaced with the DCS - please elaborate the requirement. | Alarm Management System shall be part of DCS |
| 9 | Design Basis - Instrumentation & Control (1190-DB-0801) | 11 of 21 | Instrument Asset Management system | Please indicate the functionalities required. | Instrument Asset Management System is higher level of system specifically used to monitor plant performance |
| 10 | Design Basis - Instrumentation & Control (1190-DB-0801) | 17 of 21 | Analyser | Please provide the specification of the analyser, along with the location i.e field / shelter etc. | Specification shall be provided as an addendum to the tender |
| 11 | Design Basis - Instrumentation & Control (1190-DB-0801) | 19 of 21 | CCTV System | Please indicate how many cameras are to be provided along with the demarcation of safe area cameras and hazardous area cameras. | Bidder shall refer to Layout and identify quantity. Minimum requirement shall meet to Instrumentation Design Basis clause. Reference document for quantity identification |
| 12 | Design Basis - Instrumentation & Control (1190-DB-0801) | 19 of 21 | Fire and Gas Detection (F & G) System | Please indicate the number of Gas Detectors, HC Detectors, H2 Detectors, H2S Detectors, Toxic gas detectors, Fire detectors, smoke and heat detectors, or the philosophy to estimate the same. | Bidder shall refer to Layout and identify quantity. Minimum requirement shall meet to Instrumentation Design Basis clause. Reference document for quantity identification shall be submitted in Technical bid |
| 13 | Design Basis - Instrumentation & Control (1190-DB-0801) | 20 of 21 | Ambient air monitoring system | Please confirm if one monitoring system at control room with SOX , NOX , CO , RSPM 10 & 2.5 , Wind velocity , humidity , temperature and rain data with one display at Gate shall be sufficient. | Bidder understanding is correct. |
| 14 | Design Basis - Instrumentation & Control (1190-DB-0801) | 20 of 21 | Stack Monitoring System | Please elaborate, what is intended. | Only ground flare is considered for this project. Stack monitoring system will be applicable for monitoring pollution data of stacks used in the plant. |
| 15 | Design Philosophy - Instrumentation & Control (1190-I-DB-0800) | 12 of 70 | Hazardous Area Classification | Please provide the Temperature Classification of the electrical enclosure intended for the same. | Zone 2, Gas Group IIA/B, Temp T3 |
| 16 | Design Philosophy - Instrumentation & Control (1190-I-DB-0800) | 30 of 70 | BS&W Analyser | As per the clause no. 3.6 it is mentioned "The BS&W analyzer to measure the water content in oil as specified in instrument data sheet." We don't found any data sheet with the tender document. Please provide the same. | Data Sheet shall be provided to Bidder as an addendum |
| 17 | Design Philosophy - Instrumentation & Control (1190-I-DB-0800) | 44 of 70 | Well side instrumentation | As per the clause no. 3.6 it is mentioned "The battery limit for instrumentation and control system shall include the wells connected to the OCS, the OCS itself with the remote monitoring and control facility from the existing Makum OCS which is around 10 kms away from the Barekuri OCS." Please provide the details (nos. and the types) of the instruments installed at the above mentioned wells. | Well side Instrumentation is part of scope of this bid (no. of wells that are physically present at the time of EPC detail engineering will be considered for monitoring of well parameters like pressure & temperature). The instruments have to be based on wireless concept, for details refer instrument design philosophy. |
| 18 | Design Philosophy - Instrumentation & Control (1190-I-DB-0800) | 45 of 70 | HART maintenance system | Please elaborate the requirement. | HMS is to diagonistise health of HART based Instruments. Bidder shall provide separate system with HMI |
| 19 | Design Philosophy - Instrumentation & Control (1190-I-DB-0800) | 46 of 70 | LCD/ Plasma type Mimic | It is mentioned "LCD/Plasma type Mimic should be considered in the control room." - Please provide the size and the subject/s to be displayed. | LCD/Plasma type Mimic size to be decided during detail engineering stage. Bidder shall bid with specific size in Technical bid |
| 20 | Design Philosophy - Instrumentation & Control (1190-I-DB-0800) | 46 of 70 | Universal type Hand-held Intrinsically Safe calibration / configuration units | Please ptovide the nos. to be considered. | 4 Nos of Universal type Hand held device shall be provided |
| 21 | Design Philosophy - Instrumentation & Control (1190-I-DB-0800) | 48 of 70 | Manual ESD & FSD Stations | Please clarify the requirement along with the numbers of stations. | Bidder shall refer to Layout and identify quantity. Manual ESD shall be provided at Entry/Exit way. FSD shall be provided at an interval of 30m through out Layout. Reference document for quantity identification shall be submitted in Technical bid |
| 22 | INSTRUMENT BULK MTO (1190-I-MT-0800) | 3 of 6 | HOLD Point | It is mentioned "Interface Cables, Cable glands, Trays are on hold. The same will be confirmed later." Please provide the same and along with the length of the FF Cable. | Bidder shall consider quantity shown in Bulk MTO |

| ELECTRICAL |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| 1 | General |  |  | Fault level at 11kV incoming supply - Please indicate | There is no 11kV incoming power supply. |
| 2 | General |  |  | Please provide the Hazardous Area Classification layout. | Area Classification Drawing will be provided as addendum. |
| 3 | General |  |  | Please provide "Design Basis for Electrical system". | Electrical Desisn Basis document is already provided. |
| 4 | General |  |  | Please provide the Soil Resistivity report. | Refer Civil discipline document for Soil Resistivity. |
| 5 | General |  |  | Height of high mast shall be provided. | 30m |
| 6 | General |  |  | In Process document Electric Heat Tracing is shown in crude piplines. However, in Electrical Load List heat tracing load has not been indicated. Please provide Load ( in kW ) for heat tracing. | Revised load list will be issued as an addendum to the Tender |
| 7 | General |  |  | In Process document Cathodic Protection is shown Tank bottom. However, in Electrical Load List CP load has not been indicated. Please provide Load ( in kW ) for CP. | Revised load list will be issued as an addendum to the Tender |
| 8 | General |  |  | In mechanical document Agitator is shown Tank bottom. However, in Electrical Load List agitator load has not been indicated. Please provide Load ( in kW ) for Agitator. | Revised load list will be issued as an addendum to the Tender |
| 9 | Load List, Drg. No.-1190-E-LL-0900-01 | 3 of 9 |  | As per load list " 2 nos. 3.15MVA,11kV/433kV, dry type Transformer ( 1 in operation & 1 in standby) shall be provided"- This does not match with Single Line Diagram - 1190-E-DW-0900, Rev-A. Also please note Design Philosophy specifies 'Oil Immersed' transformer. Please confirm the type of Transformer. | Revised SLD & load list will be issued as an addendum to the Tender |
| 10 | Load List, Drg. No.-1190-E-LL-0900-01 | 7 of 9 |  | As per load list " 2 nos. UPS, rating is 50kW for control room & 30kW for Compressor. As per SLD, 1no. UPS (10kVA) & 1 no. DC UPS whose rating is not reflected in Load List. Please confirm how many UPS are there and what is their rating. | Revised drawing will be issued as an addendum to the Tender |
| 11 | Load List- Load Summary & SLD- Notes & Legend Sheet | 3 of 4 |  | In Load List - "Power Generation system shall be with 1:3 Operating (1 in operation and 2 in standby) shall be provided". In Notes-1 & 2 of SLD contradict the above statement. Please clarify. Also please refer to 1190-P-SH-0100-Utility Consumption Schedule, Rev-C, where the GEG rating is shown as 2MW. Please clarify. | 2. Two gas engine driven of 2MW each in 1R+1S. Revised load list will be issued as an addendum to the Tender |
| 12 | Overall Plot Plan, Drg. No.-1190-L-DW-0400 |  |  | We are considering Substation size as per plot plan. Please provide the Electrical Equipment Layout in Substation Bldg. | Elect. Eqpt layout will be provided as addendum |
| 13 | Overall Plot Plan, Drg. No.-1190-L-DW-0400 |  |  | As per Plot plan, the substation & control room size is 45mx35m. We need the dimension of substation building and control room separately including height. | Dimensions of Sub-station and Control room will be provided. |
| 14 | Overall Plot Plan, Drg. No.-1190-L-DW-0400 |  |  | Watch Tower (WT-1, 2, 4) is shown in the drawing, where is WT-3? Please clarify. | Total number of watch tower is 3 only.( WT-3 no more exists) |
| 15 | Overall Plot Plan, Drg. No.-1190-L-DW-0400 |  |  | Diesel Generator and Distribution Transformer location are not shown in Overall Plot Plan. | It will be indicated in the eqpt layout drawing |
| 16 | SLD - 1190-E-DW-0900, Rev-A | 4 of 4 |  | Short circuit current at 415V Bus. Please indicate | Revised drawing will be issued as an addendum to the Tender |
| 17 | SLD - 1190-E-DW-0900, Rev-A | 4 of 4 |  | We are considering GTG, Distribution Transformer, DG, UPS rating as per load list & SLD. | Accepted. Any additional load requirement envisaged during detail engineering needs to be considered by contractor. |
| 18 | SLD - 1190-E-DW-0900, Rev-A | 4 of 4 |  | The DC UPS rating is not mentioned. Plesae provide the rating. | Revised drawing will be issued as an addendum to the Tender |
| 19 | SLD - 1190-E-DW-0900, Rev-A | 4 of 4 |  | Please indiacte busbar material ( Al / Cu ) for HT & LT switchboard. | Both Aluminum or Copper are acceptable. |
| 20 | SLD - 1190-E-DW-0900, Rev-A | 4 of 4 |  | The Voltage grade of GTG is 6.6 kV. How it will directly feed the power to 415V Bus? Please clarify. | There is no 6.6kV system in the plant. The generator is 415V. Transformer rquired 415V is applicable. |
| 21 | SLD - 1190-E-DW-0900, Rev-A | 4 of 4 |  | ACB rating of DG Set incomer is 5000A and bus rating is 2500A, 415V. Is it OK? Please clarify. | Revised drawing will be issued as an addendum to the Tender |
| 22 | SLD - 1190-E-DW-0900, Rev-A | 4 of 4 |  | The voltage ratio of lighting transformer is 415V/240V and connected to LDB bus of 415V. How? Also please note that in Electrical design Philosophy rating of lighting transformer is 415V/415V. Please clarify. | The lighting Transformer is 415V / 240V. |
| 23 | SLD - 1190-E-DW-0900, Rev-A | 4 of 4 |  | 1250A, 11kV ACB. Is it ACB or VCB/SF6.? Please clarify. | This shall be VCB only. This will be indicated in the revised SLD. |
| 24 | SLD - 1190-E-DW-0900, Rev-A | 4 of 4 |  | What is the desired limit of power factor improvement ? | The power factor shall be 0.99 |
| 25 | SLD - 1190-E-DW-0900, Rev-A | 3 of 4 |  | "Trip / Interlock signals shall be provided for each Power Transformer"- Is there any Power Transformer in this electrical system? Please clarify. | Contractor understanding is correct. Trip / interlock signals shall be provided for each transformers. |
| 26 | SLD - 1190-E-DW-0900, Rev-A | 4 of 4 |  | As per SLD UPS out put voltage is 240V AC whereas in Instrument design basis the UPS output voltage is 110 AC. Please confirm. | Revised drawing will be issued as an addendum to the Tender |
| 27 | Electrical Design Philosophy, Doc. O-1190-E-DB-0900. | 25 of 37 |  | As per Electrical Design Philosophy, we understand that the substation shall have 2.5m cable cellar / vault. We need the dimension of cable celler / vault except height. | This shall be decided during detailed Engineering. |
| 28 | Electrical Design Philosophy, Doc. O-1190-E-DB-0900. | 14 of 37 |  | Please provide 'Project Design Data Sheet' as mentioned in Design Philosophy. | Please refer Process design basis for project design data. |
| 29 | Electrical Design Philosophy, Doc. O-1190-E-DB-0900. | 16 of 37 |  | Please provide the OIL Standard Specification for equipment. | Reference document will be provided as addendum. |
| 30 | Electrical Bulk MTO, Doc No.-1190-E-MT-0900. | 4 of 8 |  | Please forward Equipment Layout, Electrical Cable Tray Layout, Electrical Lighting Layout, Electrical Earthing Layout, Electrical cable schedule and Electrical lighting loop, Junction box construction and mounting diagram details as mentioned in MTO "Note-1". | These documents are part of detailed engineering documents. |
| 31 | Electrical Bulk MTO, Doc No.-1190-E-MT-0900. | 6 of 8 |  | MTO specifies MV cables with XLPE insulation whereas Design Philosophy specifies PVC insulated cables. Please confirm. | MV cables shall be PVC insulated. |
| 32 | Electrical Bulk MTO, Doc No.-1190-E-MT-0900. | 4 of 8 |  | Please provide the client's Cable Specification. | Will be provided as an addendum |
| 33 | Electrical Bulk MTO, Doc No.-1190-E-MT-0900. | 4 of 8 |  | Please provide the OIL installation details | Will be provided later to the final selected bidder. |
| 34 | SLD - 1190-E-DW-0900, Rev-A | 4 of 4 |  | Please confirm how many Gas Turbine Generators are to be supplied under this contract - 2 or 3. | 2. Two gas engine driven of 2MW each in 1 Running + 1 Standby |
| 35 | SLD - 1190-E-DW-0900, Rev-A | 4 of 4 |  | Please confirm the type of generator - Gas Turbine Generator or Gas Engine Generator. | Gas Engine Generator. |
| 36 | SLD - 1190-E-DW-0900, Rev-A | 4 of 4 |  | As per SLD we understand that11kV incoming supply from SEB will be fed to 3.15MVA Transformer. How? Shall we consider one number 2(two) Pole structure for 11kV over head line in Plant battery limit? Or will the 11kV supply be provided by cable by SEB? | There is no HV system in the plant, capacitor is required for only LV. Revised SLD will be provided as an addendum. |
| 37 | SLD - 1190-E-DW-0900, Rev-A | 4 of 4 |  | Please confirm the scope of supply of the incoming 11kV cable/ overhead line. In case it is to be supplied under this contract the approximate length of 11kV cable is required if it is through cable OR the location of 2Pole structure in case of OH line. | There is no HV system in the plant, capacitor is required for only LV. Revised SLD will be provided as an addendum. |
| 38 | SLD - 1190-E-DW-0900, Rev-A | 4 of 4 |  | The current rating of the line connecting GTGs to the 415V Switchboard is 5000A. For this high current Busduct is to be provided. The SLD does not indicate busduct connection. Please confirm. Four number busduct connection are required to connect 3nos. GTG and 1no. Transformer to the 415V Switchgear. With the existing layout routing of busduct will be quite difficult. The length of busducts are also quite high and busducts are costly items. Please confirm busduct connection for the above. | There is no bus duct connection for switchgear only cable connections. Revised SLD will be provided as an addendum. |
| 39 | SLD - 1190-E-DW-0900, Rev-A | 4 of 4 |  | Short Circuit level at 415V bus is approximately 100kA. Please suggest vendors who manufacture 100kA Type Tested Switchboards in India. | Revised SLD will be provided as an addendum. Provided Short circuit current rating. |
| 40 | SLD - 1190-E-DW-0900, Rev-A | 4 of 4 |  | Please provide capacitor rating in car for APFC Panel. | Revised SLD will be provided as an addendum. Provided APFC rating. |
| 41 | SLD - 1190-E-DW-0900, Rev-A | 4 of 4 |  | Please provide kVA rating of DC UPS. | Revised SLD will be provided as an addendum. Provided DC UPS rating. |
| 42 | SLD - 1190-E-DW-0900, Rev-A | 4 of 4 |  | Typical motor feeder is shown in Emergency Main DB. Please clarify 'IR' & 'PC' as shown in feeder and which motors are to be taken in to account. | Please check the electrical load list. Which is required emergency power it's mentioned in electrical load list. |
| 43 | 1190-E-LL-0900-02 - ELECTRICAL EQUIPMENT LIST |  |  | The Electrical Equipment List does not list Major Electrical Equipment. Please provide the list. | Revised Electrical Equipment List will be provided as an addendum. |
| 44 | 1190-L-DW-400 - Equipment Layout-Overall Plot Plan | 1 of 1 |  | As per Plot Plan we are not considering any lighting for future area. | Noted |
| 45 | Lighting fixture |  |  | We are considering metal halide lamp for flood light, street light, highbay & mediumbay lighting fixture as the discontinue of HPMV lamp from manufacturer. | metal halide lamp shall be considered for outdoor(High Mast). HPSV lamp shall be considered for street light. Revised Electrical Design basis will be issued. |