| Technical Query | Reply From OIL |
| --- | --- |
| Technical clarification of Thermal engineering 1.Please provide the local meteorological data, including but not limited to the following items: the average wind speed in summer (winter); average annual temperature; extreme maximum temperature; extreme minimum temperature; the summer air conditioning calculation dry bulb (wet bulb temperature; the outdoor design temperature for summer(winter) ventilation; the outdoor design temperature for Heating,etc. 2.Referred to sheet 4 of 4 in document 1190-E-DW-0900 ，single line diagram shows 3 set Gas Turbine Generator and each 3.25MW，but the PROCESS DESCRIPTION in document 1190-P-GD-0100-01 describes 2 set Gas Turbine Generator and each 2MW. Please determine the quantity and the total output of Gas Turbine Generator. 3.Please determine the cooling method about the cooling system of Gas Turbine Generator, air cooling or water cooling? 4. Please determine whether the building to be built need Heating? 5. Please determine the air conditioning system, split air-conditioning system or central air – conditioning system? | - Basic Engineering and FEED has been done based on metrological data. Please refer to 1190-P-GD-0100-04 - Two Nos. Gas Engine Driven Gensets (one running, one standby) , 2 MW each - Preferably Air cooling. To be confirmed by Vendor - Room heating not required - Split air-conditioning |
| Technical Query | Reply From OIL |
| Technical clarification of Electric Engineering - It is described in 1190-E-0900 Rev.B Page 17, all transformers except lighting transformers shall be oil immersed, but in 1190-E-GD-0900-01 Rev.C , the outdoor use transformer is the dry type. What’s more, the rated voltage ratio is 11kV/433V, but in figure 1190-E-DW -0900 Rev.A, the rated voltage ratio is 11kV/415V. Please clarity. - The Gas Turbine Generator output voltage is 6.6kV in figure 1190-E-DW -0900 Rev.A, but the output bus voltage is 415V, Please clarity. 3、In 1190-E-0900-01 Rev.C, there are two transformers (one in operation and one in standby), but in 1190-E-DW-0900 Rev.A, there is only one transformer. Please provide another transformer’s function and single line diagram. 4、Please clarity whether the 3.15MW 6.6Kv/415kV transformer is included in the design range, whether the main function of the transformer is to provide the power supply for this project. 5、The lighting transformer (rated ratio is 415V/240V ) output voltage is 240V in figure 1190-E-DW -0900 Rev.A, but the output bus voltage is 415V, Please clarity. 6、Please clarity the specific values of HV and MV voltage level. whether the HV refers to 6.6kV and MV refers to 415V. 7、Please clarity the different power range of motors corresponding to different startup modes. | - Should be Oil immersed & the rated voltage ratio is 415V. - 415 V only. Revised drawing will be issued as an addendum to the Tender. - Follow SLD, Revised drawing will be issued as an addendum to the Tender. - There is no requirement for 6.6kv/415V transformer in plant. - The lighting Transformer ration is 415V/240V - Revised SLD will be issued as an addendum for clarity.. 7) Please refer Electrical Design Basis. |

| Technical Query | Reply From OIL |
| --- | --- |
| Technical clarification of Anti-corrosion Engineering 1. Kindly provide the technical specification 1190-M-SP-502-05; 2. Kindly provide the technical specification 6732-000-MW-SP-7403-00; 3. Kindly clarity scope of sacrificial anode protection system, the internal wall of the tank or the external wall of the tank. 4. Kindly provide the technical specification for sacrificial anode protection. | 1. Painting. Specification “1190-M-SP-502-05” to be issued as an addendum. 2. Technical specification 6732-000-MW-SP-7403-00 is not valid. Will be removed 3. Internal wall of the tank and underneath of tank Bottom plate. 4. Specification for sacrificial anode protection will be issued as an addendum. |
| Technical clarification of Mechanic engineering 1. Please confirm the type of generator set, gas engine driven generator set or gas turbine generator, and confirm the voltage grade of generator set, 6.6kV or low voltage(400V). Described in the tender documents as follows: i) In Process Design Basis(1190-P-DB-0100), Process Description(1190-P-GD-0100-01), generator set is gas engine driven generator. ii) In appendix 4 of Utility Consumption Schedule(1190-P-DB-0100), generator set is turbine generator. iii) In Single Line Diagram(1190-E-DW-0900), generator set is gas turbine generator. 2. Please confirm the quantity of gas generator set. Described in the tender documents as follows: i) In Process Design Basis(1190-P-DB-0100)& Process Description(1190-P-GD-0100-01)& Utility Consumption Schedule(1190-P-DB-0100) 2.12/note-3,two number of 2MW gensets(one running & one standby) will provided in this project, and one more additional 2MW genset in future to be procured separately by OIL. ii) In appendix 4 of Utility Consumption Schedule(1190-P-DB-0100), the operation mode of gensets is one in operation and two in standby, total of three. iii) In Single Line Diagram(1190-E-DW-0900), the quantity of gas gensets is three. | - Gas engine driven generator & KAVIN to correct the documents accordingly. - Two gas engine driven of 2MW each in 1R+1S philosophy and space should be kept for installing the third 2MW generator in future. Also all provision for evacuating power from the future generator should be provided by the EPC in line with the other two generators. KAVIN to correct the documents accordingly. |
| 3. Please confirm the power of gas gensets. Described in the tender documents as follows: i) In Process Design Basis(1190-P-DB-0100)&Process Description(1190-P-GD-0100-01)&Utility Consumption Schedule(1190-P-DB-0100)2.12/note-3&Captive power plant(1190-P-DW-1301), two gas gensets(one running & one standby) will provided in this project, and the power of one gas genset is 2MW. ii)In Single Line Diagram(1190-E-DW-0900), the quantity of gas gensets is three, parameters of one genset is 3.25MW, 6.6kV, 3PH, 50Hz,0.8pf; iii) In Equipment List(1190-M-LL-0500), the quantity of gas gensets is two, one running & one standby, the power of one genset is 2000kW. 4. Please confirm the location of emergency Diesel Generator Set and specific requirements of diesel fuel system. Described in the tender documents as follows: In appendix 4 of Utility Consumption Schedule(1190-P-DB-0100), one Diesel Generator Set will provided, the rating power is 1000kW, but the installation area of diesel generator set is not found in Equipment Layout(1190-L-DW-0400), and diesel fuel system for Diesel Generator Set and Fire Water Pump is not found in the tender documents. | - 2 Nos. Gas Engine Gensets , 2 MW each 4. Contractor shall decide the location of the Emergency DG Set near to sub-station and layout shall be submitted for approval during EPC |
| Technical Query | Reply From OIL |
| Technical clarification of Civil Engineering 1.Is procurement of material supply, such as bricks and aluminum alloy, from local or domestic? 2.Does the building's exterior need insulation processing? ( Energy Saving Treatment) 3.Who is responsible for the external supporting facilities? | 1 Upto EPC 2 NO 3 Contractor themselves. |
| Technical Query | Reply From OIL |
| Technical clarification of Communication engineering 1.Which is Communication backbone network, Radio communication or Fibre optic cable? 2.Cisco of referred to EPC TENDER other accessories which is brand or communication protocol ? 3.Please state explicitly communication interface，Who is responsible for the external supporting facilities? 4.Kindly provide the technical specification for Exchanger and transmission equipment. | 1EPC to propose for company’s acceptance. 2. Cisco is the brand name. 3 Contractor themselves. 4 Vendor’s standard is acceptable |
| Technical Query | Reply From OIL |
| Technical clarification of Geological exploration Engineering 1.The scope and content of the Pre-Engineering Survey against IS code/standard. 2.Referred to” 3.4 water table” of 1190-S-RP-0600 Soil Investigation Report, the Standing Water Level ranges from 5.5m to 6.0m below the ground level, but the water level is considered at ground level in the “liquification calculation”, why? 3.Referred to” 8. 0 Recommendation and Conclusion” of 1190-S-RP-0600 Soil Investigation Report, the field is divided into 5 areas, so it’s necessary for Kavin to show the boundary of these areas in survey drawing. | 1. Question not clear 2. Bidder to follow tender Document. 3. Boundary shall be shown in addendum. |
| Technical Query | Reply From OIL |
| Technical clarification of Water Treatment engineering 1.Referred to the 1190-P-DB-0100 at page 17 of this tender document, only four analysis items (pH, Salinity, Carbonate and Bi-Carbonate) were found in the produced water analysis. Please provide full produced water quality analysis report(including of chloride, suspending solid, temperature, O/W, etc) due to the requirement of corresponding produced water treatment system design verification. 2 Referred to the 1190-P-DB-0100 at page 20 of this tender document, sludge content is not required for the treated effluent water. Please confirm if the oil content in the water is the only requirement for the treated effluent. 3. Referred to the 1190-P-DB-0100 at page 49 of this tender document, the pressurized potable water is from deep tube well/shallow tube well header. Please provide this water quality analysis report as design basis of portable water treatment plant. 4. Referred to the 1190-P-GD-0100-01 at page 29 of this tender document, the size of produced water hydrocyclone has been specified as 457.2I/D×1517T/F. The detailed and final dimension/sizing should be hold at this moment. | - As mentioned already, Bidder to design the system based on given produced water analysis in the tender documents. - Sludge content is required for treatment. “Sludge : NIL” refers to NIL sludge content in the treated water. Same way Oil in water content must be less than 10 ppm in the treated water. 3. Water sample data in EPC scope. - As mentioned already, As per sizing, the given size is acceptable, however size will be confirmed by vendor during detailed engineering. |
| Technical Query | Reply From OIL |
| 5.Referred to the 1190-P-GD-0100-01 at page 38 of this tender document, rain water and spilled oil in the process area will be drained into a effluent water collection pit whose capacity is 60 m3(5000(L) X 4000(W) X 3000(H)). Please provide the rain flow in this process area or local rainfall intensity for pit storage capacity and rain water collection time verification.The Gas Turbine Generator output voltage is 6.6kV in figure 1190-E-DW -0900 Rev.A, but the output bus voltage is 415V, Please clear. 6.Referred to the 1190-P-GD-0100-01 at page 39 of this tender document, the water from deep tube well is filled into fire water storage tank. Please confirm that well water is clear with little amount of particle(Generally there is a particle remove facility between water well and fire water storage tank to secure particle number in the water) 7. Referred to the 1190-P-GD-0100-01 at page 50 of this tender document, the portable water filter is vertical cartridge type. In the practice, as the case maybe, other types may be suitable for specified water depending on water analysis report as requested above. | - 5. Oil spills and rainwater from process system are collected in bund wall and routed to effluent water collection pit. Rain flow from process area, local rainfall intensity will be determined by EPC contractor during detailed engineering. Based on the rain flow from process area, EPC contractor shall determine the pit storage capacity. - 6. Water analysis of deep tube well will be done during detailed engineering by EPC contractor and potable water shall comply WHO regulations. - 7. As per our consideration, we have used vertical cartridge filter, bidder to advise suitable filter based on water analysis report. - & 9. It shall be discussed with RO vendor to decide whether buffer tank is required or not. . |
| 8. Referred to the 1190-P-DW-0110 of this tender document, product water from RO system is routed to portable water pump directly. Based on our experience, one buffer water tank is recommended to be set between RO system and potable water tank to secure RO elements. 9.Referred to the 1190-P-DW-0110 of this tender document, product water from RO system is routed to portable water pump directly. Based on our experience, one buffer water tank is recommended to be set between RO system and potable water tank to secure RO elements. 10.Referred to the 1190-P-DB-0100 at page 48 of this tender document, potable water capacity is calculated based on 100 US Gallon/per person/ day for total 80 persons, which is equivalent to 8000 US Gallon per day (30.28KLPD). However, we also find that the capacity of both UV system (ZZZ-1420) and potable water pumps (ABJ-1390) is 600KLPD from PFD drawing 1190-P-DW-0110. This capacity (600KLPD) is much more than the calculated one (30.28KLPD). Please check and confirm it. experience, RO system recovery rate should be achieve approximate 70-75% with this deep tube water quality, therefore please check and review it. There is not mechanical data sheet of portable water pump. Please consider compact UV installations which can be installed in the pipes instead of current type since the smaller footprints and same performance of the latter. 11.Referred to the 1190-P-GD-0100-05 at page 9 of this tender document, Plant Effluent Treatment System is required to handle oily contaminated water collected by open drain system. However, we cannot find this PETS in any P&ID or PFD drawing. In addition, PETS system has been deleted in the equipment list. Please confirm whether PTES is needed or not. If not, please explain requirement of this part. | 8/9. Not required 10. The potable water pumps are only for filling of potable water tank and the capacity given as 600 KLPD stands correct. The RO system outlet flowrate shall be 600KLPD and UV sterilization unit inlet capacity shall be 600KLPD. 11. Refer to 1190-P-DW-0104. The effluent water system contains the Effluent water collection pit. This water is pumped to the Produced water treatment system 1190-P-DW-0102 |
| Technical Query | Reply From OIL |
| Technical clarification of Instrumentation Engineering 1. According to process data, there is no sulfur in the proposed OCS，but it refers to H2S in 1190-I-DB-0800 INST DESIGN PHILOSOPHY Rev-C (04.July.2014),page 48 of 70,line 6. 2. In view of the reliability and timeliness of the field bus signals, it is suggested that the key control loop and interlock in ESD system adopts hardwires. 3. Please provide the technical specification for control systems(PLC/ESD/F&G system). | 1 No sulphur is there 2 ESD signals are NON FF but control loops (related to control valves) will be in FF 3 EIL specifications to be followed, Shall be provided |
| Technical Query | Reply From OIL |
| Technical clarification of Gas engineering 1.Referred to 1190-P-DB-0100 Process Design Basis, Rev-C (09.July.2014) at page 11, the gas composition of well fluid is a range ,please confirm which kind of composition we can use. 2.Referred to 1190-P-DB-0100 Process Design Basis, Rev-C (09.July.2014) at page 11, the gas composition of well fluid is not content the h2o, please confirm . 3.The LP GAS COMPRESSOR PACKAGE don’t have the PID and PFD ,please provide the detailed PID and PFD drawings, if not provided, whether to need to carry on the detailed design. 4. please confirm LP GAS COMPRESSOR PACKAGE are included which equipment and number. 5.It is not present the separator in the layout of LP GAS COMPRESSOR PACKAGE. 6. Please confirm the component of fuel gas after treatment, especially for the component of the H2O. 7. The size of the equipment has given , the selected device whether the size must be in accordance with the design requirements in the bid. | - Detailed Engineering to be carried out based on provided range. - H2O Content: Since it is associated Gas, H2O Content will be a part of the fluid. The fluid is a combination of Oil + Gas + Water. Hence, Water Content provided along with incoming Crude Characteristics to be considered. - Schematic P&ID provided. Compressor Package is a vendor supplied package. Data sheet will be provided - CZZ-1470 A/B - Question not clear - Fuel Gas Filter separators to remove particles of 2 microns and above. Mist Extractor to remove the moisture content if any. - Sizes are provided based on basic engineering. Actual sizes to be confirmed after detailed Engineering and to be approved by EPMC/OIL |
| Technical Query | Reply From OIL |
| Technical clarification of Surveying and Mapping engineering 1. 25 + OCS, compressed file provided in the 18. Structural topographic Survey report - B (1190 - S - RP - 0601 Topographical Survey Report_B. PDF), not A report? 2.In addition to the station (Gas station and wellsite) of surveying and mapping, there is no other professional surveying and mapping requirements "?Such as: all kinds of line measurement includes: dry air feeder, single well gas line, dry water feeder, transmission and distribution lines, cable and optical fiber cable line and road measurement. | - Question not clear - Question not clear |
| Technical Query | Reply From OIL |
| Technical clarification of Process Engineering 1. It is said that about 25 to 30 wells will be drilled in 1190-P-DB-0100. However, the instruction mentions that there are 28 high pressure wells and 14 low pressure wells, which is 42 wells in total. Thus, please check the number of wells in total? 2. (1190-P-DW-0101 SHEET: 5 of 7)Reverse demulsifier is added to the liquid which is from HP/LP manifold outlet before bath heater to achieve rapid separation of oil and water,but in general it should be added to the positive phase demulsifier ,please confirm this clearly. 3. According to the documents（P-1190 HEAT & MASS BALANCE TABLE REV-C ，sheet：7ofof），treated Crude oil temperature is 46 ℃，viscosity is 13.43CP(13.43mPa.s)，there are very good liquidity under this conditions.Why did you addviscosity reducer to pump outlet? | - To design as per the instructions i.e. for 28 HP and 14 LP wells. - Please follow FEED and Basic Engineering 3. To care of winter effect on Crude Viscosity. To design as per Basic Engineering please. |

| Technical Query | Reply From OIL |
| --- | --- |
| 4. The FEED design documents lack of project site meteorological data、site topography、 engineering geological data ，whether the survey measurements are included in the scope of work，please confirm this clearly. 5. Whether the selection of equipment suppliers must be selected in the recommended list.Most of the equipmentsare very mature and reliablein process design applicationin our country. Is it possibleto usethe equipment of our country?please confirm this clearly. 6. Please provide the number of continuous operation days in OCS | 4. The Basic Engineering has been carried out by EPMC based on Metrological data, Topography etc. Please refer to 1190-P-GD-0100-04 5. Equipments to be procured as per the Vendor List. 6. 24 X 7 X 365 |
| Technical Query | Reply From OIL |
| Technical clarification of Structural Engineering 1. Used in the calculation of standards is available Chinese standard or American standard. 2. Corrosion and Fireproof paint according to Chinese standards, and whether the use of Chinese goods. 3. Which main materials can choose in China or locally，such as concrete, masonry, steel and steel products. Please provide the level, grade, size and modulus of locally main materials. 4. Please provide a local practice of foundation and foundation treatments. | - Please follow standards mentioned in the Engineering Documents as per the Tender. - Painting standard and material shall be as per Specification for Painting. Specification for Painting to be issued as an addendum. - All materials shall be from provided Vendor`s list. - To follow codes and standards as per Civil and Structural design Philosophy 1190-S-DB-0600 and any other Code mentioned in the Tender. |