| INSTRUMENTATION |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| 1 |  |  |  | Please provide the data sheets for the following items as the same is not available with bid documents: 1. Flow Instruments ( Ultrasonic Flow meter, Turbine Flow meter , DP Flow Transmitter, Mass Flow meter, Rotameter, Magnetic Flow meter,Flow Element, Restriction Orifice, Flow Indicator, Orifice Flow Transmitter) 2. Level Instruments (Level Transmitter Displacer Type, Radar Type, Level Gauges-Magnetic ,Reflex Type, Level Switch; , DP Level Transmitter, Level Transmitter Magnetic Type, Level Switch,). 3. Pressure Instruments ( Pressure Transmitter, Pressure Gauge, Differential Pressure Gauge) 4. Temperature Instruments ( Temperature Transmitter, Temperature Gauge, 5.ANALYZER (OIL IN WATERANALYSER) 6. Valve ( Control Valve, Pressure Safety Valve, Shut down Valve, On- Off Valve, Self Actuated Pressure Control Valve) 7. Please provide I/O List . | 1 to 6. Process Data sheets will be provided as an addendum. 7. IO list shall be prepared by Bidder based on Instrument Index provided in the tender |

| ELECTRICAL |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| 1 | Electrical |  | For 10 KVA UPS system | For 10 KVA UPS system, please provide the followings:- (1) Battery back up period required for AC & DC UPS systems not mentioned in ‘Design Philosophy’ and ‘Single Line diagram’ docs. Please provide the required back-up period? 2)Type of Batteries mentioned are VRLA. We assume these are 12V SMF VRLA Batteries ( Exide/ Amara Raja/ Suntech ) and not 2V SMF VRLA type ( HBL/ Amara Raja ). Please Confirm? 3)The ‘Electrical Load List’ confirms the total UPS load as 93.57 KVA whereas SLD mentions AC UPS rating as 10KVA and No rating specified for DC UPS. Please clarify? 4) Kindly provide the specifications for Industrial UPS with IP 41/42 . | - back up time for DC supply is 2 hrs & AC suplly is 4 hrs. 2) 12V lead acid batteries. 3) Contractor is advised to calculate the UPS load based on latest available/revised loads.(Revised Load list will be issued as an addendum) 4) Specification will be provided |
| 2 | Electrical |  | For 110 V DC UPS | For 10 V DC UPS, please provide the followings:- 1)Load Current & Battery capacity 2)You need FC or FCBC Charger. Please Confirm? 3)Any specified specification from the end user for 10 V DC UPS. Please provide? | Specification will be provided as addendum |
| 3 | Electrical |  |  | For power & control cables construction specified in MTO & in tender specification is not matching. Kindly clarify / confirm which is to be followed? | Bidder to confirm the reference document number where this disparity is found. |
| 4 | Electrical |  |  | For cable trays, thickness is not specified. Please provide the thickness of cable tray to be used? | 2mm thick heavy duty. Ladder / Perforated type cable trays made up of material Hot Dipped Galvanized iron. |