| INSTRUMENTATION |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| 1 | IFB No: CPG5284P15 | Page-121/ f | Entire Fire Hazard area | Bidder Requires Plant Fire & Gas Detection layout, Specification & Datasheet for estimation. | Fire & Gas detection layout shall be developed during detailed engineering. However the specification and quantity of detectors will be given as an addendum to the tender. |
| 2 | IFB No: CPG5284P15 | Page-121/ g | Automatic Fire Detection | Bidder Requires Fire Detection & Alarm System Control Room layout, Specification & Datasheet for estimation. If same required in Sub-station then provide layout. | Spec. For F & G alarm system, Layout will be provided as an addendum to the tender. |
| 3 | IFB No: CPG5284P15 | Page-124/ a | Intrusion detection / security system | As scope defined only for surveillance cameras, bidder understands that there is no intrusion required. Confirm the bidder understanding. Bidder requires CCTV Layout / CCTV block diagram, specification & Datasheet for estimation. | Surveillance cameras only are required. Quantity, layout and spec. of the CCTV cameras will be given as an addendum to the tender. |
| 4 | IFB No: CPG5284P15 | Page-93/ 4.6.1 | Tank Farm Management system, Flow metering system, Multi phase flow meter, Motorized valve | Bidder requires specification & datasheet of subject packages for estimation. | Standard specification for Tank Farm Management will be provided as an addendum to the tender. Datasheet will be provided as an addendum |
| 5 | General |  | Hook-up & Installation Dwgs | Bidder requires Hook-up & Installation drawings for validate of Instrument Bulk MTO. | The quantities indicated in the MTO are indicative only for bidding purposes. Bidder to prepare the H/up and installation drawings considering this as basis. |
| 6 | 1190-I-MT-0800 |  | INSTRUMENT BULK MTO | Bidder want to understand that, the estimated Bulk MTO for Tran-A only or Combination of Train A & Train B. | Estimated Bulk MTO is for one train only. Revised MTO will be provided as addendum |
| 7 | 1190-I-DB-0801 | Page-7/1.5 | DESIGN BASIS-INSTRUMENTATION & CONTROL. | Specification defined PLC shall be Triple Modular Redundant, Bidder will propose Quad system. Please confirm your acceptance. | Main offer shall be for TMR. QMR shall be considered with approval of OIL/EPMC during detail engineering. |
| 8 | General |  | Access Control System/PAGA System | Access Control System/PAGA System is not envisaged for this project. Confirm the Bidder understanding. | Access Control is not envisaged. But PAGA is required. |
| 9 | General |  | Instruments & Valves | Bidder requires Specification & datasheet of all type of Instruments & Valves envisaged in this project. | Bidder shall consider valves and instruments as per the typical data sheets provided. Process Data sheets will be provided as an addendum to the tender. |
| 10 | General |  | I/O List | Bidder requires I/O list of DCS, ESD & F&G PLC for estimation. | Bidder shall refer Instrument Index provided for the IO quantity. |
| 11 | 1190-P-DW-0204 |  | P&ID | In note-8, mentioned that some of the SDV’s are for future scope, so bidder has to know I/O’s for same to be considered in his scope or not? Kindly confirm the requirement. Other some P&ID’s also like same, Please confirm for that also. | IOs to be considered for future scope as well. |
| 12 | 1190 -I-DB-0800 | DESIGN PHILOSOPHY-INSTRUMENTATION & CONTROL | Control room instrumentation | Bidder Understand that, Wells Monitoring & Control is not part of tender hence Bidder will not consider in his scope of supply & installation of any wireless instrument, surveillance facility & wireless RTU at wells as well as at Barekuri OCS. Bidder requested same to be removed from Dwgs-1190-I-DW-0800-01. | Well monitoring is part of tender based on wireless instrumentation philosophy. Bidder to quote accordingly, however no well control is envisaged. |
| 13 | 1190 -I-DB-0801 | CONSTRUCTION OF BAREKURI OCS DESIGN BASIS-INSTRUMENTATION & CONTROL | CONSTRUCTION OF BAREKURI OCS DESIGN BASIS-INSTRUMENTATION & CONTROL | Bidder understand that, there is no scope of Offshore wells hence requirement of Interaction with Offshore wells, Remote monitoring from Offshore Control Room & ESD facilities from Offshore Control Room is Null & not in Bidder’s scope. | Offshore wells are not in scope. |
| 14 | 1190 -I-DB-0801 | CONSTRUCTION OF BAREKURI OCS DESIGN BASIS-INSTRUMENTATION & CONTROL | CONSTRUCTION OF BAREKURI OCS DESIGN BASIS-INSTRUMENTATION & CONTROL:- Operating philosophy: (As per P&ID | Below Packages is not part of tender & listed in documents hence this document required to be revised & issue for Estimation. 1. Emulsion Treater, 2.Online pollution Monitoring system, 3. Chlorinator, 4.Inert Gas Generator System | Question not clear |
| 15 | 1190 -I-DB-0800 | DESIGN PHILOSOPHY-INSTRUMENTATION & CONTROL | CONSTRUCTION OF BAREKURI OCS DESIGN PHILOSOPHY INSTRUMENTATION & CONTROL | In this document it is mentioned that, The ESD PLC shall be Foundation Field bus based for ensuring safety in operating the station and Dwgs-1190-I-DW-0800-01 ( Control System Scheme ) indicate that ESD PLC with connection of Foundation field bus Field devices. Whereas PID’s are not indicating any Field devices as FF connected to ESD PLC. Bidder requires understanding ESD PLC is FF bus based with FF devices or HART/Conventional based system with HART field devices. | ESD PLC should be a SIL certified Safety PLC & not FF based system. Only BPCS system should be FF BASED. All ESD field devices should be non-FF & HART/4-20ma devices. |
| 16 | 1190 -I-DB-0801 | CONSTRUCTION OF BAREKURI OCS DESIGN BASIS-INSTRUMENTATION & CONTROL | CONSTRUCTION OF BAREKURI OCS DESIGN BASIS-INSTRUMENTATION & CONTROL | In Hazardous area, Field Devices protection is intrinsically safe, if devices are intrinsically safe then confirms the requirement of intrinsically safe barrier. | Please follow tender requirements. Engineering standards to be followed for selection of barrier concept & selection of IS instrument will also depend on “hazardous area classification” drawing. |
| 17 | 1190 -I-DB-0801 | CONSTRUCTION OF BAREKURI OCS DESIGN BASIS-INSTRUMENTATION & CONTROL | CONSTRUCTION OF BAREKURI OCS DESIGN BASIS-INSTRUMENTATION & CONTROL | In Hazardous area, intrinsically safe protection is EEx ia OR EEx ib to be considered for estimation. | Please follow tender requirements. Engineering standards to be followed for selection of barrier concept & selection of IS instrument will also depend on “hazardous area classification” drawing. |
| 18 | 1190 -I-DB-0801 | CONSTRUCTION OF BAREKURI OCS DESIGN BASIS-INSTRUMENTATION & CONTROL | CONSTRUCTION OF BAREKURI OCS DESIGN BASIS-INSTRUMENTATION & CONTROL | In this section it is mentioned that, ESD PLC shall SIL required, Bidder require to know the SIL rating of ESD PLC. | SIL study is in EPC scope. |
| 19 | 1190-I-GD-0800 | DESIGN PHILOSOPHY-INSTRUMENTATION & CONTROL | INSTRUMENT INDEX CONSTRUCTION OF BAREKURI OCS | In this list, Instrument tags having design pressure of 250 kg/cm2g and operating range is 21-35 kg/cm2g, Bidder require to understand what design pressure to be consider for selection of Instruments. | Should be designed for 250kg/cm2 for Manifold area. |
| 20 | 1190-I-GD-0800 | DESIGN PHILOSOPHY-INSTRUMENTATION & CONTROL | INSTRUMENT INDEX CONSTRUCTION OF BAREKURI OCS | In this list, so many instrument tags have not provided instrument ranges & units, Bidder require all these data to get quotation from vendor. | Will be provided as addendum. |
| 21 | 1190-I-GD-0800 | DESIGN PHILOSOPHY-INSTRUMENTATION & CONTROL | INSTRUMENT INDEX CONSTRUCTION OF BAREKURI OCS | AS PER NOTE-1, DESIGN PRESSURE OF 40 KG/CM2G IS CONSIDERED BASED ON ARRIVAL PRESSURE OF 21-35 KG/CM2G. Bidder requires understanding the design pressure 250 kg/cm2g is considered in index sheet, so confirm the pressure to be considered for selection of instrument. | Should be designed for 250kg/cm2. |
| 22 | IFB No: CPG5284P15 | Bid Package (Page-123/ 9) | Data communication & security access control facility | Whatever facility ( radio, Intrusion detection, security, computers, Telephone ) for this system is in OIL’s scope as defined in this documents, Confirm the bidder understanding | It is in EPC scope. |
| 23 |  |  | Control Room Layout | Bidder requires control room layout details for estimation. | Will be issued as addendum |
| 24 |  |  | Cable routing/Cable Tray Layout | Bidder requires Cable routing/Cable Tray Layout details for estimation. | Will be issued as addendum |
| 25 | 1190 -I-DB-0800 | DESIGN PHILOSOPHY-INSTRUMENTATION & CONTROL | Control room instrumentation | Bidder Understand that, Wells Monitoring & Control is not part of tender hence Bidder will not consider in his scope of supply & installation of any wireless instrument, surveillance facility & wireless RTU at wells as well as at Barekuri OCS. Bidder requested same to be removed from Dwgs-1190-I-DW-0800-01. | Well monitoring is part of tender based on wireless instrumentation philosophy. Bidder to quote accordingly, however no well control is envisaged. |
| 26 | 1190 -I-DB-0801 | CONSTRUCTION OF BAREKURI OCS DESIGN BASIS-INSTRUMENTATION & CONTROL | CONSTRUCTION OF BAREKURI OCS DESIGN BASIS-INSTRUMENTATION & CONTROL | Bidder understand that, there is no scope of Offshore wells hence requirement of Interaction with Offshore wells, Remote monitoring from Offshore Control Room & ESD facilities from Offshore Control Room is Null & not in Bidder’s scope. | Offshore wells are not in scope. |
| 27 | 1190 -I-DB-0801 | CONSTRUCTION OF BAREKURI OCS DESIGN BASIS-INSTRUMENTATION & CONTROL | CONSTRUCTION OF BAREKURI OCS DESIGN BASIS-INSTRUMENTATION & CONTROL:- Operating philosophy: (As per P&ID | Below Packages is not part of tender & listed in documents hence this document required to be revised & issue for Estimation. 1. Emulsion Treater, 2.Online pollution Monitoring system, 3. Chlorinator, 4.Inert Gas Generator System | Question not clear |
| 28 | 1190 -I-DB-0800 | DESIGN PHILOSOPHY-INSTRUMENTATION & CONTROL | CONSTRUCTION OF BAREKURI OCS DESIGN PHILOSOPHY INSTRUMENTATION & CONTROL | In this document it is mentioned that, The ESD PLC shall be Foundation Field bus based for ensuring safety in operating the station and Dwgs-1190-I-DW-0800-01 ( Control System Scheme ) indicate that ESD PLC with connection of Foundation field bus Field devices. Whereas PID’s are not indicating any Field devices as FF connected to ESD PLC. Bidder requires understanding ESD PLC is FF bus based with FF devices or HART/Conventional based system with HART field devices. | ESD PLC should be a SIL certified Safety PLC & not FF based system. Only BPCS system should be FF BASED. All ESD field devices should be non-FF & HART/4-20ma devices. |
| 29 | 1190 -I-DB-0801 | CONSTRUCTION OF BAREKURI OCS DESIGN BASIS-INSTRUMENTATION & CONTROL | CONSTRUCTION OF BAREKURI OCS DESIGN BASIS-INSTRUMENTATION & CONTROL | In Hazardous area, Field Devices protection is intrinsically safe, if devices are intrinsically safe then confirms the requirement of intrinsically safe barrier. | Please follow tender requirements. Engineering standards to be followed for selection of barrier concept & selection of IS instrument will also depend on “hazardous area classification” drawing. |
| 30 | 1190 -I-DB-0801 | CONSTRUCTION OF BAREKURI OCS DESIGN BASIS-INSTRUMENTATION & CONTROL | CONSTRUCTION OF BAREKURI OCS DESIGN BASIS-INSTRUMENTATION & CONTROL | In Hazardous area, intrinsically safe protection is EEx ia OR EEx ib to be considered for estimation. | Please follow tender requirements. Engineering standards to be followed for selection of barrier concept & selection of IS instrument will also depend on “hazardous area classification” drawing. |
| 31 | 1190 -I-DB-0801 | CONSTRUCTION OF BAREKURI OCS DESIGN BASIS-INSTRUMENTATION & CONTROL | CONSTRUCTION OF BAREKURI OCS DESIGN BASIS-INSTRUMENTATION & CONTROL | In this section it is mentioned that, ESD PLC shall SIL required, Bidder require to know the SIL rating of ESD PLC. | SIL study is in EPC scope. |
| 32 | 1190-I-GD-0800 | DESIGN PHILOSOPHY-INSTRUMENTATION & CONTROL | INSTRUMENT INDEX CONSTRUCTION OF BAREKURI OCS | In this list, Instrument tags having design pressure of 250 kg/cm2g and operating range is 21-35 kg/cm2g, Bidder require to understand what design pressure to be consider for selection of Instruments. | Should be designed for 250kg/cm2 for Manifold area. |
| 33 | 1190-I-GD-0800 | DESIGN PHILOSOPHY-INSTRUMENTATION & CONTROL | INSTRUMENT INDEX CONSTRUCTION OF BAREKURI OCS | In this list, so many instrument tags have not provided instrument ranges & units, Bidder require all these data to get quotation from vendor. | Will be provided as addendum. |
| 34 | 1190-I-GD-0800 | DESIGN PHILOSOPHY-INSTRUMENTATION & CONTROL | INSTRUMENT INDEX CONSTRUCTION OF BAREKURI OCS | AS PER NOTE-1, DESIGN PRESSURE OF 40 KG/CM2G IS CONSIDERED BASED ON ARRIVAL PRESSURE OF 21-35 KG/CM2G. Bidder requires understanding the design pressure 250 kg/cm2g is considered in index sheet, so confirm the pressure to be considered for selection of instrument. | Should be designed for 250kg/cm2. |

| ELECTRICAL |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| 1 | 1190-E-DB-0900 | 3.1 | Area classification and equipment selection | Contractor request company to specified the type of protection for each type of electrical equipment for Zone-1 and Zone -2 area | All Equipment protection shall be followed as per IS-5571 & IS 5572 ( Annex E and IS-15142). |
| 2 | 1190-E-DB-0900 | 3.2/3.3 | Power system design /Capacity of Electrical System | Please find attached for the power distribution scheme as per the Load list. Please confirm our proposal | Please provide attachment for us to confirm/ clarify. |
| 3 | 1190-E-DB-0900 | 3.6 | System earthing | Contractor propose to use 400A, 10Sec, NER for 6.6KV generator neutral earthing . Please confirm our proposal | There is no 6.6KV system in the plant. The generator is 415V. |
| 4 | 1190-E-DB-0900 | 3.9 | Protection and Metering diagram | Contractor request company to provide the .basic protection and metering diagram for each system voltage level and motor feeders | Company will provide the detail to successful bidders. Bidders may follow general industry standard for bidding purposes. |
| 5 | 1190-E-DB-0900 | 3.13 | Power factor improvement | Please specify the minimum power factor to maintain. | Power factor shall be 0.99 |
| 6 | 1190-E-DB-0900 | 4.3 | Switchgear | Contractor not clear about the spare requirement for HV panel as no HV panel as per tender SLD. | Atleast 20% of spare shall be maintained in each number of type of outgoing feeder. |
| 7 | 1190-E-DB-0900 | 4.6 | Batteries | Please specify the type of battery. | Lead Acid Battery. |
| 8 | 1190-E-DB-0900 | 4.7 | DC Power supply system | Please specify the backup time for DC power supply | Back up time shall generally be considered as 2 hours. |
| 9 | 1190-E-DB-0900 | 4.8 | UPS | Please specify the backup time for AC UPS | Back up time shall generally be considered as 4 hours. |
| 10 | 1190-E-DB-0900 | 4.9 | Motors | Contractor understands all motors shall be with DOL starting method only. If any special type starter please specify in the load list | All Low Voltage motors starting methods DOL starting. If VFD is required, it shall be mentioned in P&ID. |
| 11 | 1190-E-DB-0900 | 4.10 | H V capacitor | Contactor understand 415V (LV) capacitor only is required and no HV capacitor is required. Please confirm our understanding | There is no HV system in the plant, capacitor is required for only LV |
| 12 | 1190-E-DB-0900 | 4.11 | Emergency Generator | Contractor considered emergency power requirement as per the load list only. Any additional load to consider company to specify | Accepted. Any additional load requirement envisaged during detail engineering needs to be considered by EPC contractor. Revised Electical Equipment list and utility PFD will be provided as an addendum. |
| 13 | 1190-E-DB-0900 | 4.13 | Cables and wires | Contractor propose to use Aluminium conductor cable for MV cable and Copper conductor for HV cables | Low voltage cables are Copper conductor only. No HV cable requirement. |
| 14 | 1190-E-DB-0900 | 4.13 | Cable and Wires | Contractor understands that unarmoured power and control cables with substation are acceptable .Please confirm our understanding. | Within substation unarmoured cable is acceptable. All other cable shall be armour type. |
| 15 | 1190-E-DB-0900 | 6.2 | Cabling system | Contactor understands that all underground cabling is directly buried. Please confirm our understanding. | Refer over all plot plans. All cable shall run through pipe rack, only special case can be accepted for direct buried. |
| 16 | 1190-E-DB-0900 | 6.2 | Cabling System | Contractor request company to specify the separation distance for power and instrument cable | Since the cables are not buried this is not applicable. |
| 17 | 1190-E-DB-0900 | 6.2 | Cabling system | Contractor request company to specify the MOC for cable tray | Cable Tray material shall be Hot Dipped galvanized iron. |
| 18 | 1190-E-DB-0900 | 6.3 | Earthing system | Contractor request company to specify the type and size of earthing cable. | Earthing cable size shall be provided. Contractor is advised to follow IS standard for earthing calculation. |
| 19 | 1190-E-DB-0900 | 6.4 | Lighting system | Contactor understanding is DC lighting is with integral battery and not with centralized DC system. Please confirm our understanding | Contractor understanding is correct. |
| 20 | General |  |  | Contractor request company to provide data sheets for following electrical equipment 1) Transformer 2) Gas engine generator 3) DG set 4) HV and LV Switchgear/ MCC 5) AC and DC UPS | Company will provide only reference document nos. contractor to prepare specification and get approval from company during detailed engineering. Data sheet to be provided as addendum. |
| 21 | General |  |  | Contractor request company to provide specification for following electrical equipment 1) Transformer 2) Gas engine generator 3) DG set 4) HV and LV Switchgear/ MCC 5) AC and DC UPS | Company will provide only reference document nos. contractor to prepare specification and get approval from company during detailed engineering. Data sheet to be provided as addendum. |
| 22 | 1190-E-DW-0900 |  | Single Line Diagram – Note 10 | Company understands that no 3.25KV circuit breaker is applicable for this project. | There is no 3.25KV in this project. Revised SLD will be provided as an addendum. |
| 23 | General |  |  | Contractor understands that no SCADA /power management system for this project including the load management system. Please confirm our understanding | Contractor understanding is correct. |
| 24 | General |  |  | Contractor request company to provide tentative substation layout | Tentative layout to be prepared by contractor. |
| 25 | General |  |  | Contractor request company to provide area classification layout and hazardous area schedule to select the electrical and instrument accordingly | Area Classification Drawing will be provided as addendum |
| 26 | 1190-L-DW-400 |  | Equipment Layout Overall plot plan | Contractor request company to provide the location of Emergency DG set | Contractor shall decide the location of the DG Set near to sub-station and layout shall be submitted for approval during EPC |
| 27 | 1190-E-DW-0900 |  | Single Line Diagram | Contractor request company to clarify the requirement of AFPC connected to emergency switch board | Yes required |
| 28 | 1190-E-DW-0900 |  | Single Line Diagram (note 2 and3) | Contractor request company to clarify the contradiction between notes and also with load list . Contractor understand only one GTG is only working at a time and other 2(two) GTG is standby. If confirm our understanding. | Contractor understanding is correct. |
| 29 | 1190-E-DW-0900 |  | Single Line Diagram (note 2 and3) | Contractor request company to clarify the contradiction between notes and also with load list. Contractor understand only one GTG is only working at a time and other 2(two) GTG is standby. If confirm our understanding. | Contractor understanding is correct. |
| 30 | 1190-E-DW-0900 |  | Single Line Diagram(Hold) | Contractor request company to clarify what is the meaning of essential and emergency DG set . Contractor understand only emergency DG of 1000KVA as per load list is required. Please confirm our understanding | There is no essential generator in the plant. Only emergency generator is required. |
| 31 | 1190-E-DW-0900 and RFQ-1190-M-TS-0512-01 |  | Gas Engine generator voltage level | As per Single line diagram generator voltage is 6.6 KV , but as per load list it is 11KV and as per RFQ for Gas engine generator the voltage level is 415V . Contractor request company to clarify the voltage rating for generator | Generator voltage level is 415V |
| 32 | 1190-E-DW-0900 and RFQ-1190-M-TS-0512-01 |  | Gas engine generator capacity | As per Single line diagram and Load list the generator rating is 3.25MW but as per equipment list and RFQ for Gas engine generator the rating is given as 2 MW . Contractor request company to confirm the rating for the generator . | 2 MW is the generator capacity of each generator. |
| 33 | 1190-E-DW-0900 |  | Single Line Diagram | It is noted that 11KV out door switchyard , but the transformer primary rating is given as 6.6KV . Contractor requesting company to clarify the same . | No Transformer required; only 415V is applicable |
| 34 | 1190-E-DW-0900 |  | Single line Diagram | Contractor not understands the requirement of emergency main switch gear shown. Contractor understand any emergency load is to connect with emergency DG set switch board | Contractor understanding is correct. Revised SLD will be provided as an addendum. |
| 35 | 1190-L-DW-400 | Over All plot plan | Outdoor switchyard | Please indicate the location of 11KV outdoor switchyard | Revised SLD will be provided as addendum |
| 36 |  |  | Cathodic Protection | Please give specific requirement for Cathodic protection requirement for the project. Please provide the standard specification if CP is required for this project. | CP is required for tanks (Only tank bottom plates) & UG piping if any. |