| PIPING |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| 1 |  |  | Specification | Please provide Insulation & Paint specifications. | Will Be provided as an addendum. |
| 2 |  | 1190-P-DB-0100 | Pressure Rating | Well fluid arrived at 35Kg/Cm2g at 300 C, but manifold system design at 250 Kg/cm2g at 800 C, please clarify. | Inlet manifold system is designed for shut in tubing pressure (250 Kg/cm2g) of well as provided by OIL. |
| 3 |  | 1190-P-DB-0100 | Ground Flare system | As per environmental condition ground flare system are obsolete, please confirm. | As per OIL preference ground flare system has been provided. |
| 4 |  |  | PID | PSV, CV sizes are under hold, please clarify. | PSV , CV sizes shall be calculated by EPC contractor during detailed engineering based on vendor’s data. |
| 5 |  | 1190-L-DW-400 Overall Plot plan | Battery Limits | Please provide battery limit point for Produced water disposal well, crude oil transfer to NHK CTF pipeline, Gas transfer line & also provide takeoff point for oil well manifolds. | To be confirmed later and issued as an addendum |
| 6 |  |  | Hot Tapping | Kindly confirm requirement of hot tapping, if any. | Hot Tapping not envisaged at this stage |
| 7 |  |  | Hazardous area classification | Please provide hazardous area classification zone layout. | will be provided as an addendum |
| 8 |  |  | Support Standard | Please provide support standards. | EPC Bidder to provide the details |
| 9 |  |  | Data Sheet | Please provide data sheet for Strainer T & Y type, Flame arrestor, Hose connector. | EPC Bidder to provide the details |
| 10 |  |  | Specification | Please provide specification for wrapping & coating for U/G piping. | will be provided as an addendum |

| FIRE FIGHTING |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Sr. No | Part No./Volume No. | Clause No./Page No/Para No. | Subject & corresponding Bid Provision | Bidder’s queries/observation/comments | Company Response |
| 1 | Piping Design Philosophy Doc No. 1190 – L - DB - 0400 | 4.2.8 Fire Fighting | - | Document, “General Civil design basis” for Fire protection guidelines is not available in tender document. | Only basic requirement is provided. EPC contractor to explore further. For Fire Protection concept, please refer P & I Ds 1190-P-DW-1001 to 1008 |
| 2 | - | - | - | Conceptual Fire Protection layout to be provided. |  |