## Sheet1
Project- Secondary TankFarm at OIL Duliajan Assam
SUBJECT : QUERY FROM BIDDER
SL.No | Type of Query | Document | Document | Clause | Subject | Bidders Query | Company Response
|  | No | Name | /Note No
1 | Mechanical |  |  |  | Plate Heat Exchanger and Cooling Tower | We had observed serious anamolies between equipment Process data sheets & the EFD provided in the tender. We are engaged in serious discussions with bath heater & EET vendors with regard to allowable fluid temperatures. We could avoid eqpt E003 which in turn would result a lesser heat duty for eqpt.E002. As per process datasheet for E002 cooling tower of approx 1200 cum/hr is called for, whereas the datasheet for cooling tower specifies a flow rate of 210cum/hr. Following receipt of inputs from upstream package vendors,we shall optimize heat duty for all heat exchangers and accordingly decide the capacity of Cooling tower. Cooling tower shall also meet the requirements of air compressor vendors who opt for watercooled design. | Kindly note that there are no anomalies in the data furnished in the tender. A by-pass line can be provided, if it is found that E-003 will not recover the heat from Dry Crude Oil coming out of the EET. Further, if it found suitable, cooling tower utilization will be reduced. This will depend entirely on the inputs from EET vendor & operation philosophy. Hence, EPC bidder to follow the tender specifications.
2 | Mechanical |  |  |  | EOT Crane | For cost effectiveness we suggest employment of Electric monorail hoist in oil circulation pump and clarified water pump sheds. | Bidder to comply as per tender specification.
3 | Mechanical |  |  |  |  | RO water shall be used in bath heaters instead of Demin water. | DM water is not envisage for Bath heaters.
4 | Mechanical |  |  |  |  | Oil circulation pump house to be relocated between the dyke adjoining T-001/T-002 /T-005 and road as header to circulation pumps is gravity fed from tanks. With the pump house in the present location the road would be blocked. | To meet gravity requirement for the pump suction,Lines shall be re-routed by removing the blind flange and routed towards north direction and followed by west (below the road as underground piping ) leading to pump house(circulation pump house 103). Lines to be considered burried at road crossingwith cushion of 1.3 mtrs from top of road to bottom of pipe. Encasing pipe sleeves for 20" line and 12" line shall be 30" and 24"respectively (Carbon steel std,ASME B36.10). All buried pipes shall be double coating and double wrapping.Pump suction lines will not be routed via pipe rack/bridge as considered in the conceptual layout.The location of the pump house remain unchanged. Pump suction lines will not travel on Pipe rack.
5 | Mechanical | TCE-7547A-300-GA-8005 |  |  |  | Please elaborate the item/eqpt to be dismantled as identified in drg no TCE-7547A-300-GA-8005. | There are no equipment to be dismantled. This is green field project.
6 | Mechanical |  |  |  |  | We feel compressed air plant of 1200 cum/hr would be sufficient to meet the needs of ETP. Separate compressor for ETP would be considered if at all necessary. | Please refer to replies issued in Corrigendum -2