| PROCESS |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 6 | Technical | Section 2- Mechanical _Section 2.1_Doc No - TCE.7547A-H-OST-300.(revised specification for RWTP) | General Requirement for Water Treatment and Water Supply | 2.2, 2.3 | Industrial and Potable Water Quality – TSS | Based on OWNER response vide TRS no 4, Process, Sr. no – 1, there is no requirement of Ultrafiltration for potable water. As per specification TSS in industrial water shall be less than 10 ppm whereas for potable water TSS shall be NIL. Considering only 5 micron activated carbon cartridge filter and UV on potable water lines, TSS in potable water as NIL may be difficult to achieve. Further please note that, as per IS-10500, there is no specific norms for TSS in potable water. Request OWNER to confirm any additional system to be considered to meet potable water TSS as NIL. | Tender specification says about quality of water required for potable water .Tender indicates the minimum requirements of system. If vendor feels the requirement to add additional equipments in the system to meet the guaranteed parameters, they may do so. However, specifications of the potable water shall be met as per tender. |
| INSTRUMENTATION |  |  |  |  |  |  |  |
| 8 | Connection Details | TCE.7547A-H-OST-300 | SCOPE OF WORK | 4.4.6 | FO cable from STF to CTF | Bidder shall only Supply FO cable. Laying, termination and commissioning of FO cable including CIVIL works from STF Control room to CTF Control room is in Client’s scope. | This is to confirm that the scope of supply, laying and integration of FO cable from STF to CTF and all related jobs appearing anywhere in the Tender stands omitted from EPC`s scope for this Tender. Bidders to take note of the same. |
| 9 | Connection Details | TCE.7547A-H-OST-300 | SCOPE OF WORK | 4.4.6 | Integration of System | Bidder understands that integration of control system at STF with control system at CTF is in Client’s scope. | This is to confirm that the scope of supply, laying and integration of FO cable from STF to CTF and all related jobs appearing anywhere in the Tender stands omitted from EPC`s scope for this Tender. Bidders to take note of the same. |