## 138-PREBID QUERY
Tender Ref: CPG6533P15
Customer Name: OIL India Limited, ASSAM
Project Name: Secondary Tank Farm
PREBID QUERIES
S.No | Doc ref | Clause | Queries | Client response
I | PROCESS
1 | TCE-7457A-CH-E-PDS | Data Sheet for Plate Heat Exchanger (E-003) | As per data sheet Specific heat value for inlet and dry crude oil is mentioned as 0.45 Kcal/Kg oC. Since operating temperature of inlet and outlet Dry crude oil varies, Specific heat value also shall varies. Bidder requests client to specify the specific heat values for inlet and dry crude oil . | No significant variation in the Specific specific heat value. Kindly consider 0.45 Kcal/kg oC as made available in PDS.
2 | Doc No. TCE.7547A-CH-300-DB-01 ,Process Design Bais | Clause 6.4 page 43 of 115 , Wet Crude oil properties | As per Clause 6.4 Crude API is given as 21.6-34. Bidder requests client to provide Exact API to follow for Design | Kindly follow the range made available in the tender documents.
3 | Corrigendum 2 | Composition of Crude oil | Bidder request Client to provide Exact composition of Crude oil. | Crude oil composition available with us was made available in corrigendum 2.
II | MECHANICAL
4 | Plate type heat Exchangers TCE .7547 A-H-OST-300 sheet 2/13 | Approved vendor list /Make- Sec 2.11 S.no 04 | Only 2 approved vendors responded for the offer , we request for the addition of following vendor too M/s IDMC Ltd | Follow tender Document
5 | Positive Displacement Pumps TCE .7547 A-H-OST-300 sheet 3/13 | Approved vendor list /Make- Sec 2.11 S.no 11 | Flowserve,Gardner & Denver,Tushaco,viking,SPX Flow,FMC,DEL PD pumps have regretted to this item. We request you to kindly add the following vendor M/s RUHRPUMPEN INDIA Pvt Ltd
6 | COOLING TOWERS TCE .7547 A-H-OST-300 sheet 3/13 | Approved vendor list /Make- Sec 2.11 S.no 12 | Most of the approved vendors were not responded , we request you for the addition of the folowing vendors 1.M/s Gem Cooling Towers Ltd 2.M/s National Cooling Towers Ltd 3.M/s Himgiri Cooling Towers
7 | Natural Gas Fired Package Boiler TCE .7547 A-H-OST-300 sheet 4/13 | Approved vendor list /Make- Sec 2.11 S.no 15 | Most of the approved vendors were found either not in range or not responded, we request you for the addition of the folowing vendors 1.M/s Thermodyne engineers Ltd 2.M/s Veesons boilers 3.M/s Matrix boilers Ltd
8 | TCE .7547 A-H-OST-300 | ETP & WTP | Request you to kindly include BGR ENERGY SYSTEMS LTD as Vendor for ETP & WTP. Enclosed the credentials for your kind perusal.
9 | Rim Seal Fire Protection TCE .7547 A-H-OST-300 Sheet 18/19 | Instrumentation & Control Sec 4.2.63 | As advised we request the following vendors for preferred vendor list for this system 1. M/s Same, Italy 2.M/s Silvani, Italy 3.M/s HD Fire Protection Systems 4.M/s Vimal Fire Protection Systems 5.M/s Vijay Fire Protection | Refer Corrigendum
III | ELECTRICAL
10 | Cathodic Protection TCE .M4-225-27 | Electrical Sec D.3.14 | We request the following vendors list for this system as we couldn’t find any approved vendors in preferred vendor list 1.M/s Corrosion Technology, UK 2.M/s Electro Protection Services India Pvt. Ltd. (EPSIPL) 3.M/s Corretech International Pvt. Ltd. 4.Cathodic Protection Co, UK | Refer Corrigendum
IV | INSTRUMENTATION
11 | Mass Flow Metres TCE .7547A-H-OST-300 | Instrumentation Sec 4.6.12 S.no. 8 | We request the following vendors to be added in the preferred vendor list, as there are only few vendors 1. M/s yokogawa 2. M/s Honeywell 3. M/s ABB | FOLLOW TENDER DOCUMENT.
12 | Ultra sonic Level Transmitters TCE .7547A-H-OST-300 | Instrumentation Sec 4.6.12 S.no. 9 | We request the following vendors to be added in the preferred vendor list 1. M/s Krohne Marshall
13 | Control Valves TCE.7547A-H-OST-300 | Instrumentation Sec 4.6.12 S.no. 14 | We request the following vendors for the same 1.M/s.SEVERN GLOCON
14 | ESD valve TCE.7547A-H-OST-300 | Instrumentation Sec 4.6.12 S.no. 24 | We request the following vendors for the same 1.M/s.SIEMENS 2.M/s.Invensys
15 | Fire & Gas detection systems TCE.7547A-H-OST-300 | Instrumentation Sec 4.6.12 S.no. 25 | We request the following vendors for the same 1.M/s.Honeywell 2.M/.Emerson 3.M/s.ABB 4.M/s.yokogawa 5.M/s.Siemens 6.M/s.Invensys
16 | Butter fly valves TCE.7547A-H-OST-300 | Instrumentation Sec 4.6.12 S.no. 16 | We request the following vendors for the same 1.M/s.Fouress Engg 2.M/.Weir BDK 3.M/s.TYCO valve 4.M/s.Inter Valve
17 | BPCS TCE.7547A-H-OST-300 | Instrumentation Sec 4.6.12 S.no. 23 | We request the following vendors for the same 1.M/s.Siemens 2.M/s.Invensys
18 | Tube fittings TCE.7547A-H-OST-300 | Instrumentation Sec 4.6.12 S.no. 34 | We request the following vendors for the same 1.M/s.champ 2.M/.Astec 3.M/s Excel Hydro
19 | Instrument Tubing TCE.7547A-H-OST-300 | Instrumentation Sec 4.6.12 S.no. 35 | We request the following vendors for the same 1.M/s.champ 2.M/.Astec 3.M/s Excel Hydro
20 | Control Panel TCE.7547A-H-OST-300 | Instrumentation Sec 4.6.12 S.no. 46 | We request the following vendors for the same 1.M/s.FOCAL AUTOMATION 2.M/.EUROCON 3.M/s.DIGITECH 4.M/s.MEGHATECH 5.M/s.JONE Controls
21 | Foundation Field Bus JBs TCE.7547A-H-OST-300 | Instrumentation Sec 4.6.12 S.no. 32 | We request the following vendors for the same 1.M/s.Baliga 2.M/s. Stahl 3.M/s.FCG 4.M/s.Sudhir switch gears
22 | Cables TCE.7547A-H-OST-300 | Instrumentation Sec 4.6.12 S.no. 31 | We request the following vendors for the same 1.M/s.orbit 2.M/s.Finolex
23 | TCE-7547A-LS-580-2003 (Corrigendum 2) | General | Final I/O count of BPCS in I/O list found not matching with that of given actual Input & Output in the list. Please clarify to finalize the i/o counts. | Refer Corrigendum.
24 | TCE-7547A-LS-580-2003 (Corrigendum 2) |  | Signals of Temperature & Pressure transmitter (which comes along with LT) are considered as digital input where as they are directly connected to radar transmitter. Please clarify. | Please proceed as per IO List.
25 | TCE-7547A-LS-580-2003 (Corrigendum 2) |  | Digital Input (DI) list is missing from MCC-BPCS, only final count is available Please clarify | Refer Corrigendum.
26 | TCE-7547A-OST-300 (4.2.64) R1 |  | No SOX measurement shall be considered for ambient air quality monitoring as per revised datasheet and TQs | SOX monitoring is not required.
27 | TCE. M4-607-07 (4.2.35) |  | Control valve follow up data sheet: 1. Kindly reconfirm the flow units against each tag no. Kg/hr or M3/hr. 2. Line size for PCV 2001 and PCV 2002 are given as 12" & 8" respectively. Based on the Cv calculations for given data , the same will need 20" & 16" sizes respectively. | 1. The flowrate for Wet Crude Oil are mentioned in M3/hr 2. Kindly follow the tender specifications.
28 | TCE.7547A-617-PI-1106 |  | The level transmitters for water tank are given as Radar type , whereas in instruments list, it is given as ultrasonic type. We will consider the same ultrasonic type suitable for water application. Kindly confirm. | Kindly proceed with ultrasonic Level transmitter.
29 | TCE.7547A-H-OST-300 | 4.2.39 | On Off / Shut down valves: Triple offset butterfly valves are required. Please note these valves are not available in the market for sizes 2" & Below. Hence we propose ball valves for these sizes. ( tag nos: XSV-2004 : 2" & XSV -2008,XV-2009 : 1" ) | Confirmed.
30 | TCE.7547A-H-OST-300 |  | PLC for package vendors: No specification is given. We propose to consider the system as per industry standard. No redundancy shall be considered for vendor package systems. | Vendor package system PLC control system philosophy shall be same as process control system philosophy
31 | TCE.7547A-H-OST-300 |  | New fire station controol room Duliajan - Kindly let us know the distance between STF and New fire station control room for laying fibre optic cable.(Rim seal fire protection ) | Refer Reply elsewhere issued earlier