## Sheet1
Project- Secondary TankFarm at OIL Duliajan Assam
SUBJECT : QUERY FROM BIDDER
SL.No | Type of Query | Document | Document | Clause | Subject | Bidders Query | Company Response
|  | No | Name | /Note No
1 | Mechanical | P&ID TCE.7547A-300-PI-8035 |  |  |  | The makeup solution marked in the P&ID shall be process water. Process water piping upto mixing tank with isolation valves shall be considered. | Confirmed. Though the Additive dosing system shown as package it is a responsibility of successful bidder.
2 | Mechanical | P&ID TCE.7547A-600-PI-1103 |  |  |  | Filtered water can not be employed for make-up in Boiler system. Instead RO water shall be used. Industrial water storage tank elevation of 12 mtrs, in our view,is low to cater to farflung consumer points in the premises.We intend employing Centrifugal transfer pumps at the outlet of Tanks 01&02 to ensure proper Distribution which implies location of the said tanks at grade level. It is deemed that potable water consumption shall be limited to Administration&canteen building. | Bidder to comply as per tender specification.
3 | Mechanical |  | Gas genset |  |  | Compact Gas genset shall be of indirect closed water cooling with radiator which eliminates employment of dedicated cooling tower. The set would be skid mounted in the open area & with acoustic enclosure to ensure noiselevel of 75dBA beyond 1mtr of equipment periphery. | Bidder to comply as per tender specification.
4 | Mechanical |  | Guard pond |  |  | We shall consider a reservoir of trapezoidal cross section in stone-pitched construction with backup HDPE net & of volume 2200 cumtr. | Not Acceptable.Bidder to comply as per tender specification.
5 | ELECTRICAL | TCE.7547A-300-PP-1000 Issue-R1 DT.12/05/2015 AND TCE.7547A-715-CT-3012 (SH.2-2) Issue-PO Dt.16/12/2014 | PLOT PLAN FOR SECONDARY TANK FARM AREA AND OVEALL CABLE TRAY LAYOUT FOR STF PLANT |  | Different Dimension | In Dwg. No.TCE.7547A-715-CT3012 (SH.1-2) Issue-PO dimension for Circulation Pump House TAG No. 103 is 20M x 8M and in Dwg. No. TCE.7547A-300-PP-1000 Issue-R1 dimension for Circulation Pump House TAG No. 103 is 31M x 8M | Bidder to follw as per Dwg. No. TCE.7547A-300-PP-1000 Issue-R1.
6 | ELECTRICAL | TCE.7547A-300-PP-1000 Issue-R1 DT.12/05/2015 AND TCE.7547A-715-CT-3012 (SH.2-2) Issue-PO Dt.16/12/2014 | PLOT PLAN FOR SECONDARY TANK FARM AREA AND OVEALL CABLE TRAY LAYOUT FOR STF PLANT |  | Different Dimension | In Dwg. No.TCE.7547A-715-CT3012 (SH.1-2) Issue-PO dimension for Dispatch Pump House TAG No. 107 is 20M x 8M and in Dwg. No. TCE.7547A-300-PP-1000 Issue-R1 dimension forDispatch Pump House TAG No. 107 is 31M x 8M | Bidder to follw as per Dwg. No. TCE.7547A-300-PP-1000 Issue-R1.
7 | ELECTRICAL | TCE.7547A-300-PP-1000 Issue-R1 DT.12/05/2015 AND TCE.7547A-715-CT-3012 (SH.2-2) Issue-PO Dt.16/12/2014 | PLOT PLAN FOR SECONDARY TANK FARM AREA AND OVEALL CABLE TRAY LAYOUT FOR STF PLANT |  | Different Dimension | In Dwg. No.TCE.7547A-715-CT3012 (SH.1-2) Issue-PO TAG No. 109 is Formation Water Tank (2 x5000KL) its dimension is Ø20M x 16.5M and in Dwg. No. TCE.7547A-300-PP-1000 Issue-R1 TAG No. 109 is Effluent Water Tank (2 x5000KL) its dimension is Ø20M x 18M | Bidder to follw as per Dwg. No. TCE.7547A-300-PP-1000 Issue-R1.
8 | ELECTRICAL | TCE.7547A-300-PP-1000 Issue-R1 DT.12/05/2015 AND TCE.7547A-715-CT-3012 (SH.2-2) Issue-PO Dt.16/12/2014 | PLOT PLAN FOR SECONDARY TANK FARM AREA AND OVEALL CABLE TRAY LAYOUT FOR STF PLANT |  | Different Dimension | In Dwg. No.TCE.7547A-715-CT3012 (SH.1-2) Issue-PO dimension for Clarified Water Tank (2 x5000KL) TAG No. 110 is Ø20M x 16.5M and in Dwg. No.TCE.7547A-300-PP-1000 Issue-R1 dimension forClarified Water Tank (2 x5000KL) TAG No. 110 is Ø20M x 18M | Bidder to follw as per Dwg. No. TCE.7547A-300-PP-1000 Issue-R1.
9 | ELECTRICAL | TCE.7547A-300-PP-1000 Issue-R1 DT.12/05/2015 AND TCE.7547A-715-CT-3012 (SH.2-2) Issue-PO Dt.16/12/2014 | PLOT PLAN FOR SECONDARY TANK FARM AREA AND OVEALL CABLE TRAY LAYOUT FOR STF PLANT |  | Different Dimension | In Dwg. No.TCE.7547A-715-CT3012 (SH.1-2) Issue-PO dimension for Fire Water Pump House TAG No. 114 is 35M x 10M and in Dwg. No. TCE.7547A-300-PP-1000 Issue-R1 dimension for Fire Water Pump House TAG No. 114 is 35M x 10M is 20M x 18M | Bidder to follw as per Dwg. No. TCE.7547A-300-PP-1000 Issue-R1.
10 | ELECTRICAL | TCE.7547A-300-PP-1000 Issue-R1 DT.12/05/2015 AND TCE.7547A-715-CT-3012 (SH.2-2) Issue-PO Dt.16/12/2014 | PLOT PLAN FOR SECONDARY TANK FARM AREA AND OVEALL CABLE TRAY LAYOUT FOR STF PLANT |  | Different Dimension | In Dwg. No.TCE.7547A-715-CT3012 (SH.1-2) Issue-PO TAG No. 115 is Fire Water Tank (CAP: 2No x3500 KL) its dimension is Ø22M x 10MHt and in Dwg. No. TCE.7547A-300-PP-1000 Issue-R1 TAG No. 115 is Fire Water Tank (CAP: 2No x3500 KL) its dimension is Ø22M x 12.0M | Bidder to follw as per Dwg. No. TCE.7547A-300-PP-1000 Issue-R1.
11 | ELECTRICAL | TCE.7547A-300-PP-1000 Issue-R1 DT.12/05/2015 AND TCE.7547A-715-CT-3012 (SH.2-2) Issue-PO Dt.16/12/2014 | PLOT PLAN FOR SECONDARY TANK FARM AREA AND OVEALL CABLE TRAY LAYOUT FOR STF PLANT |  | Different Dimension | In Dwg. No.TCE.7547A-715-CT3012 (SH.1-2) Issue-PO dimension for Parking Area TAG No. 118 is 20M x 10 M and in Dwg. No. TCE.7547A-300-PP-1000 Issue-R1 dimension forParking Shed TAG No. 118 is 201M x 5M | Bidder to follw as per Dwg. No. TCE.7547A-300-PP-1000 Issue-R1.
12 | ELECTRICAL | TCE.7547A-300-PP-1000 Issue-R1 DT.12/05/2015 AND TCE.7547A-715-CT-3012 (SH.2-2) Issue-PO Dt.16/12/2014 | PLOT PLAN FOR SECONDARY TANK FARM AREA AND OVEALL CABLE TRAY LAYOUT FOR STF PLANT |  | Final Name of Building | In Dwg. No.TCE.7547A-715-CT3012 (SH.1-2) Issue-PO TAG No. 119 is Office & Admin Building and in Dwg. No.TCE.7547A-300-PP-1000 Issue-R1 Tag No.119 is Admin & Canteen Building | Bidder to follw as per Dwg. No. TCE.7547A-300-PP-1000 Issue-R1.
13 | ELECTRICAL | TCE.7547A-300-PP-1000 Issue-R1 DT.12/05/2015 AND TCE.7547A-715-CT-3012 (SH.2-2) Issue-PO Dt.16/12/2014 | PLOT PLAN FOR SECONDARY TANK FARM AREA AND OVEALL CABLE TRAY LAYOUT FOR STF PLANT |  | Different Dimension | In Dwg. No.TCE.7547A-715-CT3012 (SH.1-2) Issue-PO dimension for Watch Tower (3 Nos) TAG No. 123 is 20M x 10 M and in Dwg. No.TCE.7547A-300-PP-1000 Issue-R1 dimension for Watch Tower (3 Nos) TAG No. 123 is 201M x 5M | Bidder to follw as per Dwg. No. TCE.7547A-300-PP-1000 Issue-R1.
14 | ELECTRICAL | TCE.7547A-300-PP-1000 Issue-R1 DT.12/05/2015 AND TCE.7547A-715-CT-3012 (SH.2-2) Issue-PO Dt.16/12/2014 | PLOT PLAN FOR SECONDARY TANK FARM AREA AND OVEALL CABLE TRAY LAYOUT FOR STF PLANT |  | Final Name of Building | In Dwg. No.TCE.7547A-715-CT3012 (SH.1-2) Issue-PO TAG No. 124 is Canteen Building o and in Dwg. No. TCE.7547A-300-PP-1000 Issue-R1 Tag No.124 is Guard Pond Di mension 40M x 40M | Bidder to follw as per Dwg. No. TCE.7547A-300-PP-1000 Issue-R1.
15 | ELECTRICAL | TCE.7547A-300-PP-1000 Issue-R1 DT.12/05/2015 AND TCE.7547A-715-CT-3012 (SH.2-2) Issue-PO Dt.16/12/2014 | PLOT PLAN FOR SECONDARY TANK FARM AREA AND OVEALL CABLE TRAY LAYOUT FOR STF PLANT |  | Discrepancy | In Dwg. No.TCE.7547A-715-CT3012 (SH.1-2) Issue-PO TAG No. 125 is Storm Water collection Tank and in Dwg. No. TCE.7547A-300-PP-1000 Issue-RO Tag No.125 is Deleted | Bidder to follw as per Dwg. No. TCE.7547A-300-PP-1000 Issue-R1.
16 | ELECTRICAL | TCE.7547A-300-PP-1000 Issue-R1 DT.12/05/2015 AND TCE.7547A-715-CT-3012 (SH.2-2) Issue-PO Dt.16/12/2014 | PLOT PLAN FOR SECONDARY TANK FARM AREA AND OVEALL CABLE TRAY LAYOUT FOR STF PLANT |  | Different Dimension | In Dwg. No.TCE.7547A-715-CT3012 (SH.1-2) Issue-PO dimension for Overhead Tank For Potable Water TAG No. 126 is Ø4M x2.5M and in Dwg. No. TCE.7547A-300-PP-1000 Issue-R1 dimension for Overhead Tank For Potable Water TAG No. 126 is Ø8.2M x 4.5M | Bidder to follw as per Dwg. No. TCE.7547A-300-PP-1000 Issue-R1.
17 | ELECTRICAL | TCE.7547A-300-PP-1000 Issue-R1 DT.12/05/2015 | PLOT PLAN FOR SECONDARY TANK FARM AREA |  | Confirmation of building and Requirment of Electricity | Tag No. 124 Guard pond, do it need any Electrical supply . Not mentioned in Tender. Hence we are not consindering the same. Kindly confirm | Confirmed
18 | ELECTRICAL | TCE.7547A-715-CT-3012 (SH.1-2) Issue-PO Dt.16/12/2014 | OVEALL CABLE TRAY LAYOUT FOR STF PLANT |  | Location of MCC | Building no 111 for Clarified water pump house. 2 MCC in building. One for Process continuous load and second for Intermittent load. As per current location cable length too long problem for voltage drop and no of cable we want to make two MCC both are process(Continuous and Intermittent as per load ) one in same room other Near building no 106 -Cooling Tower + Heat exchanger. Proposed location is technoeconomical and good for maintenace hence kindly accept. | MCC is located with Minimum Distance/ clearance from Tanks as per OISD Standard. Bidder to follow the same.
19 | ELECTRICAL | TCE.7547A-715-CT-3012 (SH.1-2) Issue-PO Dt.16/12/2014 | OVEALL CABLE TRAY LAYOUT FOR STF PLANT |  | Location of CPP, Substation and control room | Building no 111 for Clarified water pump house. 2 MCC in building. One for Process continuous load and second for Intermittent load. As per current location cable length too long problem for voltage drop and no of cable we want to make two MCC both are process(Continuous and Intermittent as per load ) one in same room other Near building no 106 -Cooling Tower + Heat exchanger. Proposed location is technoeconomical and good for maintenace hence kindly accept. | Substation and CPP is located with Minimum Distance/ clearance from Tanks as per OISD Standard. Bidder to follow the same.