## TRS-1
PROJECT: EPC OF STF WITH DEHYDRATION FACILITY AND ETP AT MADHUBAN, DULIAJAN- IFB NO. CPG6533P15
CLIENT : OIL INDIA LIMITED, DULIAJAN
SUBJECT : PRE BID QUERY (TECHNICAL)
SL.No | Type of Query | Document | Document | Clause | Subject | Bidders Query | Company Response
|  | No | Name | /Note No
1 | GAS ENGINE RATING | Section II Mechanical -1 Corrigendum No. 2 | GAS ENGINE - DATA SHEET A Reply to Technical Queries TRS-1 | 2.0 DESIGN CONDITIONS Point No. 15 of 20 | No’s and minimum Output at generator terminals given as 4 x 1400 KW We understand that the rated power factor is 0.9 hence the gas genset capacity is 1600 KVA at 0.9 p.f. - CONFIRMED | As per Datasheet A minimum capacity of each Genset shall be 1400 KW. However, in replies to TQs it has been confirmed that Genset rating shall be 1600 KVA at p.f.0.9. This translates to minimum Genset rating of 1440 KW. Bidder request owner to kindly confrim the Rating of the Gas Engine Genset. | Bidder to follow as per Tender Data sheet A for min capacity of each genset rated at site condtion menitoned as 1400 kW.
2 |  |  | Tender Corrigendum-2 | Technical Replies / Sheet TRS1 / Sr No. 14 | Oily water treatment Package details has been claried as: Oily water treatment is different from ETP. Oily water treatment package and Contaminated Rainwater treatment package is a combined package but separate from ETP. The output water quality shall match the ETP output water characteristics. It may have similar equipment. Design, equipments Philosophy for the same has to be finalized by bidder. | The Contaminated Rain Water will have free float oil and no emulsified oil will be present in the feed to OWS. The design of the OWS need not be as per the P&ID No. TCE.7547A-300-PI-8037, R0. Most of the equipment mentioned in the P&ID will not be required. As confirmed in the Tender Corrigendum-2 we will finalize the design of the OWS which shall ensure the out put treated water quality. | Confirmed (However, bidders to note that OWS output treated water quality shall match the ETP output water characteristics).
3 |  | TCE.7547A-300-PDS-8704 | Process data sheet for Electrostatic Emulsion Treater | Notes, Point no:-13 | The note -13 mentions the followings: " Electrostatic Emulsion Treaters (EETs) & Bath Heaters (refer PDS doc. No. TCE.7547A-300-PDS-8705) are considered as separate equipment for Dehydration Unit. However Dehydration Unit comprising of Bath Heater and EETs in a single (combined) equipment will be preferred." | Bidder understand that instead of providing separate Electrostatic Emulsion Treater and Bath Heater for dehydration of Crude a common dehydration unit comprising of both Electrostatic Emulsion Treater and Bath Heaters can be considered provided it meets the process requirement. Please confirm | Note no. 13 is self explanatory.
4 | Approved Vendor |  | Approved vendor List | Foam Pump | The following vendors appearing in the tender approved vendor list: FIRETECH HD Fire VISHAL | None of the vendor mentioned in the approved vendor list are manufacturer of foam pumps as required for the project. Kindly provide us the list of approved makes | The vendors provided in the list are package vendor for foam system equipments. The make which is provided by the package vendor are accepatable.
5 | Approved Vendor |  | Approved vendor List | Engine Driven reciprocating Pumps |  | The tender approved vendor list does not mention any makes for Gas Engine driven high pressure reciprocating pumps. Kindly provide us the list of approved makes | We have mentioned the vendor list for pumps & Gas Engines separately.bidder to follow the same.
6 | Approved Vendor |  | Approved vendor List | Motorized Gate Valves | The tender approved vendor list for Instrumentation & Controls does not mentins any makes for Motorized Gate Valves. However it mentions separate makes for Gate Valves and Actuators. The approved makes for Gate Valves are mentioned as follows: M/s. L&T Ltd. M/s. Penberthy Inc. M/s. Dresser Inc. M/s. Virgo Valves M/s.Flowserve Limited | None of the vendors except L&T manufactures Gate Valves. In order to make a competetive proposal we need have multipe proposals. Bidder proposes to consider the approved makes for Valves in the Approved vendor list for Mechanical Items for Gate Valves | Actuator vendor will do the assembly of both body valve & actuator. Bidder is not expected to approach actuator vendor and Valve vendor seperately.
7 |  | TCE.7547A-H-OST-300 & SLD for STF Plant - TCE.7547A-715-AU-3001, Rev-P0 | 8 OF 20 - SECTION - 3.1 | 2.6.1 | Voltage Drop: The combined voltage drop between PCC to MCC and MCC to motor/Loads 5% during running. Cable from PCC-3 to MCC-4 | MCC-4 (Process MCC - INT) is located in Clarified Water PH MCC Room which is approximately 450M distance from PCC-3. The rating of the incomer circuit breaker is 2500A. Also the voltage drop from PCC to Motor/Load is to be restricted to 5%. If we select the cable from PCC-3 to MCC-4 assuming even 4% voltage drop for 2500A, the number of cables are coming very much of higher size. This will not only be uneconomical, there will be difficulty in termination of so many number of cable and higher sizes in PCC-3 and MCC-4. We, therefore, propose to install 2nos 1.8MVA, 415/433V Dry type transformer inside the Clarified Water PH besides the MCC-4 and select the cable based on current carrying capacity. Please confirm. We also propose to size the incomer cable to all MCCs from PCCs based on the working load on MCCs and not as per the incomer Circuit breaker current rating of all MCCs. Kindly confirm. | Bidder to comply as per Specification. Bidder to comply the design criteria for sizing the cable in the Speification.
8 |  | TCE.7547A-H-OST-300 | 40 of 57 | Sl. No. O (i) / SECTION: 4.1 of Instrumentation Design Philosophy & Sl. 27 / 35 of Instrumentation - Cables Datasheet, Section-4.2.68, | Material - Inner Seath / Outer Sheath | As per Sl. No. O (i) of Instrumentation Design Philosophy, "ESD and FGS cables shall be Fire resistance as per IEC 60331." where as as per Instrumentation - Cables Datasheet all Power Cable, Control Cable, Signal Cable and Traid Cable are specified as Extruded Flame Returdant PVC IEC-332, Type ST-2, 90 deg C as IS-5831. Bidder understands that all the instrumentation cables mentioned above are as per the data sheet i.e. Extruded Flame Returdant PVC IEC-332, Type ST-2, 90 deg C as IS-5831. Accrodingly Bidder shall not consider any Fire resistance (Fire Safe) cables for any Instrumentation and communication purpose. Kindly confirm Bidder understanding. If ESD and FGS cables need to be of Fire resistance (Fire Safe) as per IEC 60331 type then kindly provide the appropriate Datasheet which is not available with the Tender. | Fire resistance cables are FRLs cables only as per IEC - 60331 & 60332 and the standard says about the testing requirements of Fire resistace cables.