## PRE BID QUERIES
S.No. | Document Reference | Section / Clause no. or Drawing no. | Subject | Description | QUERY | TCE Response
1 | Pre - bid Queries Response | Cost Breakup Annexure A _ Revised | Excel Sheet , Mechanical A1.11 | Pressure Reducing stations (2 Nos for Wet Crude Oil & 2 No for Natural Gas). | Kindly review and confirm Pessure reducing station requirement for Natural Gas. We understand and as per the P&ID NO TCE.7547A-300-PI-8020, Only one PRS is required for 17 Kg Pressure Natural Gas Line | Confirmed.
2 | Pre - bid Queries Response | Cost Breakup Annexure A _ Revised | Excel Sheet , Process B1.5 | Dry Crude Oil Dispatch Pump with Gas Engine | It is appearing at two place in same Process section. We considering only one. Please confirm | Confirmed. (P-003 A/B/C/D)
3 | Pre - bid Queries Response | Ammendment 2 Part 1 | Technical Queries response TRS 2; Point No12 | Laboratory facility at STF is in EPC Scope and shall be as per tender requirements. | Please provide details on the Laboratory setup required at Duliajan STF.List of Testing Instruments . | The lab should have the following facilitities to test amongst other standard parameters required to ensure quality of crude and water: i. BS&W Content ii. Salinity iii. pH iv. xCO2, x CO3 v. Density vi. Viscosity vii. API Gravity viii. Pour Point ix. TDS (ETP) x. Oil & Grease (ETP) xi. TSS (ETP) Testing instruments in the scope of EPC, which shall be validated by EPMC/OIL.
4 | Pre - bid Queries Response | TRS 5 , Point No 1 | BOD and COD in Raw Effluent | Please consider the BOD as 80-135 mg/l and COD as 180-1400 mg/l in the inlet of effluent treatment plant. There is no requirement of maintaining BOD & COD in treated water from ETP. However, in order to meet desired BOD/COD parameter at the inlet of UF, the bidder is free to suggest his own scheme. | Please note that with respect to the BOD as 80-135 ppm, COD should not vary so widely (180-1400 PPM). Unless any industrial waste is being added. Please clarify | Kindly follow range BOD as 80-135 mg/l and COD as 180-1400 mg/l.
[5 empty] | so then it should also be clarified that design inlet BOD / COD value (Average OR Maximum ?). | This is a range.
[5 empty] | For further meeting the inlet BOD/COD limit for UF system it is recommended that the revised treatment scheme should be common for every bidder. Hence we feel that a revised ETP process scheme should be released by the TCE/ OIL | ETP Process needs to maintain BOD & COD, hence whatever required for the system to run effectively shall be decided by ETP vendor / bidder. The scheme attached to the tender document is tentative & shall be firmed up by successful bidder.
5 | DWG TCE 7547A-300-PP-1201 (Sh 3 of 3) | Conceptional Piping Layout ; Section C- C |  | a) at BOB EL 7250 : accomodating 10 pipes with Cable tray b) at BOB EL 5500 : accomodating 4 pipes with future pipe | Please note that there is an ambiguity in the BOB EL . Please confirm which one has to be followed. (Please check sheet 1 of this excel sheet for better understanding) | Section mentioned in Conceptual Piping Layout is to be followed.
| TCE.7547A-715-CT-3012 (SH.2-2) | Over all cable tray layout ; section C-C |  | a) at BOB EL 8250 : accomodating 9 pipes with Cable tray a) at BOB EL 7250 : accomodating 5 pipes with Cable tray b) at BOB EL 5500 : accomodating 4 pipes with future pipe